## Initial
The results listed on this page are from residential homes in Chicago that have volunteered to have their water tested for lead as part of a research study. The data that is shown below is quality controlled. The study is ongoing, and the results below are a small portion of the large sample population necessary for statistical evaluation. The data below will be further reviewed prior to inclusion in statistical evaluation. The results are anonymized to the block level, so the complete address of each home is not posted. In cases where a sample tests over 15 parts per billion (the action limit set by the EPA), the Department of Water Management will contact the homeowner to discuss the results and schedule a time to resample the water and inspect the home’s plumbing and electrical wiring to better evaluate possible causes. All results are shown in PPB (Parts per Billion). In cases where multiple homes on the same block have results, the location is further amended as "Site 1", "Site 2", etc.
Date Sampled | Address | Multiple Sites | Geographic Coordinates | 1st Draw | 4th Draw | 6th Draw | 5 Minute Flush | 5 Minute Flush Duplicate
2016-09-28 | 10000 S. Eggleston Ave. Chicago, IL 60628 |  |  | 1.9 | 1.4 | 1.5 | 1.3
2016-09-28 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 1.9 | 1.5 | 1.8 | 0.8
2017-01-10 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 1.8 | 1.1 | 1.1 | 0.7 | 0.7
2017-02-08 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 2.0 | 1.1 | 1.2 | 0.6
2017-03-07 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 2.1 | 1.0 | 1.0 | 0.7
2017-04-04 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 1.7 | 1.1 | 1.1 | 0.8
2017-05-09 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 2.1 | 1.5 | 1.4 | 1.2
2017-06-06 | 10100 S. Eggleston Ave. Chicago, IL 60628 |  |  | 1.4 | 1.0 | 1.1 | 0.9
2017-06-20 | 10100 S. Racine Ave. Chicago, IL 60643 |  |  | 3.1 | 4.7 | 4.4 | 2.7
2016-09-28 | 10200 S. Eggleston Ave. Chicago, IL 60628 | Site 1 |  | 3.8 | 7.6 | 10 | 4.7
2017-01-10 | 10200 S. Eggleston Ave. Chicago, IL 60628 | Site 1 |  | 4.1 | 4.2 | 7.9 | 1.8
2016-10-12 | 10201 S. Eggleston Ave. Chicago, IL 60628 | Site 2 |  | 5.5 | 8.0 | 13 | 5.3
2017-01-12 | 10201 S. Eggleston Ave. Chicago, IL 60628 | Site 2 |  | 4.8 | 4.8 | 8.4 | 2.3
2016-09-29 | 10202 S. Eggleston Ave. Chicago, IL 60628 | Site 3 |  | 1.9 | 1.0 | 0.9 | 0.6
2017-01-11 | 10202 S. Eggleston Ave. Chicago, IL 60628 | Site 3 |  | 1.8 | 1.9 | 1.9 | 0.8
2016-09-15 | 10300 S. Racine Ave. |  |  | 5.5 | 5.0 | 18 | 4.5
2016-10-08 | 10300 S. Racine Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-11-01 | 10300 S UNION AVE |  |  | 1.8 | 5.1 | 7.0 | 1.2
2017-11-01 | 10300 S LOWE AVE |  |  | 3.0 | 2.2 | 1.6 | 1.3
2016-09-15 | 10XX W. 103rd St. |  |  | 6.4 | 2.6 | 4.0 | 2.0
2017-11-02 | 104XX S ARTESIAN AVE |  |  | 2.4 | 2.3 | 4.3 | 1.1
2017-11-17 | 104XX S ARTESIAN AVE | Site 1 |  | 5.3 | 2.5 | 2.3 | 0.8
2017-02-08 | 104XX S. Artesian Ave. | Site 2 |  | 3.7 | 2.0 | 3.3 | 1.3 | 1.2
2017-03-08 | 104XX S. Artesian Ave. | Site 2 |  | 3.2 | 3.6 | 3.9 | 1.2
2017-07-28 | 105XX S. Racine Ave. | Site 1 |  | 4.4 | 3.9 | 12 | 8.4
2017-08-08 | 105XX S. Racine Ave. | Site 2 |  | 4.3 | 6.8 | 7.6 | 4.3
2017-06-20 | 106XX S. Racine Ave. |  |  | 1.2 | 2.6 | 2.5 | 2.3
2017-06-23 | 107XX S. Ave. N |  |  | 5 | 14 | 12 | 3.1
2017-07-21 | 107XX S. Ave. N |  |  | 5.8 | 23 | 15 | 4.4
2017-09-06 | 107XX S. Ave. N |  |  | See Follow-Up Sequential Sampling Table for Results
2017-04-04 | 11XX W. 104th St. |  |  | 4.4 | 2.6 | 2.3 | 0.6
2017-04-14 | 11XX W. 104th St. |  |  | 1.2 | 1.0 | 1.1 | 0.7
2017-08-23 | 11XX W. 19th Pl. |  |  | 2.2 | 4.2 | 6.2 | 2.7
2016-08-25 | 11XX E. 81st St. | Site 1 |  | 2.0 | 2.2 | 1.8 | 1.2 | 1.2
2016-12-15 | 11XX E. 81st St. | Site 1 |  | 3.8 | 3.3 | 13 | 1.0
2016-08-25 | 11XX E. 81st St. | Site 2 |  | 1.2 | 1.9 | 2.9 | 0.9
2016-12-15 | 11XX E. 81st St. | Site 2 |  | 0.8 | 1.2 | 2.5 | 0.4 | 0.3
2017-06-20 | 11XX W. 102nd St. |  |  | 3.1 | 3.0 | 8.1 | 1.8 | 1.8
2017-04-14 | 12XX W. 97th St. | Site 1 |  | 1.0 | 2.6 | 3.3 | 1.2
2017-10-26 | 12XX W. 97th St. | Site 1 |  | 2.9 | 2.4 | 4.0 | 2.1
2017-12-14 | 12XX W. 97th St. | Site 1 |  | 3.0 | 1.4 | 1.2 | 0.9
2017-04-14 | 12XX W. 97th St. | Site 2 |  | 2.2 | 2.7 | 4.2 | 0.8
2017-11-02 | 12XX W. 97th St. | Site 2 |  | 6.0 | 3.7 | 9.6 | 1.4
2017-12-14 | 12XX W. 97th St. | Site 2 |  | 3.8 | 3.2 | 4.2 | 0.9
2017-04-17 | 12XX W. 97th St. | Site 3 |  | 5.1 | 11 | 11 | 7.4
2017-04-13 | 12XX W. 97th St. | Site 4 |  | 1.1 | 1.5 | 1.7 | 0.9
2017-11-08 | 12XX W. 97th St. | Site 4 |  | 1.0 | 1.5 | 1.3 | 0.9
2017-05-12 | 12XX W. 97th St. | Site 5 |  | 0.9 | 0.9 | 0.9 | 0.7
2017-10-27 | 12XX W. 97th St. | Site 5 |  | 1.3 | 0.9 | 1.9 | 2.2
2017-04-21 | 12XX W. 97th Pl. | Site 1 |  | 1.7 | 2.2 | 2.7 | 1.3
2017-04-13 | 12XX W. 97th Pl. | Site 2 |  | 4.3 | 6.5 | 6.5 | 1.4
2017-10-26 | 12XX W. 97th Pl. | Site 2 |  | 3.8 | 3.9 | 4.3 | 2.1
2017-06-01 | 12XX W. 97th St. | Site 6 |  | 0.8 | 0.8 | 1.1 | 0.6
2017-10-26 | 12XX W. 97th St. | Site 6 |  | 0.8 | 1.1 | 1.3 | 0.8
2017-12-06 | 12XX W. 97th St. | Site 6 |  | 0.9 | 1.1 | 1.3 | 0.6
2017-04-21 | 12XX W. 97th Pl. | Site 3 |  | 2.0 | 2.5 | 2.6 | 1.1
2017-11-03 | 12XX W. 97th Pl. | Site 3 |  | 2.8 | 4.9 | 8.1 | 2.1
2017-12-05 | 12XX W. 97th Pl. | Site 3 |  | 3.0 | 4.2 | 6.6 | 1.7
2017-04-14 | 12XX W. 97th St. | Site 7 |  | 4.3 | 4.0 | 3.9 | 1.4
2017-10-27 | 12XX W. 97th St. | Site 7 |  | 2.4 | 4.6 | 4.2 | 3.1
2017-04-14 | 12XX W. 97th Pl. | Site 4 |  | 1.2 | 1.2 | 2.5 | 0.7
2017-10-26 | 126XX S YALE AVE |  |  | 8.8 | 11 | 13 | 6.4
2017-12-14 | 126XX S YALE AVE |  |  | 9.6 | 5.4 | 5.5 | 3.5
2017-04-14 | 13XX W. 97th St. | Site 1 |  | 2.5 | 2.2 | 2.3 | 1.2
2017-10-26 | 13XX W. 97th St. | Site 1 |  | 2.6 | 2.6 | 2.2 | 0.9
2017-12-05 | 13XX W. 97th St. | Site 1 |  | 1.7 | 3.7 | 1.6 | 0.7
2017-04-13 | 13XX W. 97th St. | Site 2 |  | 7.2 | 4.5 | 4.3 | 1.7
2017-11-02 | 13XX W. 97th St. | Site 2 |  | 3.7 | 5.2 | 6.0 | 2.6
2017-04-14 | 13XX W. 97th St. | Site 3 |  | 1.4 | 1.6 | 4.2 | 0.9
2017-10-26 | 13XX W. 97th St. | Site 3 |  | 2.0 | 2.7 | 6.2 | 2.4
2017-04-14 | 13XX W. 97th St. | Site 4 |  | 1.5 | 1.2 | 1.3 | 0.9
2017-11-03 | 13XX W. 97th St. | Site 4 |  | 2.0 | 1.5 | 1.4 | 1.5
2017-12-14 | 13XX W. 97th St. | Site 4 |  | 1.9 | 2.0 | 2.3 | 1.2
2017-04-14 | 13XX W. 97th St. | Site 5 |  | 2.6 | 4.9 | 4.8 | 2.4
2017-10-26 | 13XX W. 97th St. | Site 5 |  | 3.6 | 7.0 | 7.1 | 5.4
2017-12-06 | 13XX W. 97th St. | Site 5 |  | 2.8 | 3.9 | 2.8 | 2.5
2017-04-19 | 13XX W. 97th Pl. |  |  | 2.0 | 1.5 | 1.6 | 1.0
2017-10-26 | 13XX W. 97th Pl. |  |  | 1.9 | 1.5 | 1.6 | 1.6
2017-04-17 | 14XX W. Touhy Ave. |  |  | 0.9 | 3.3 | 6.4 | 0.3
2017-05-08 | 14XX W. Touhy Ave. |  |  | 1.8 | 5.8 | 4.5 | 0.5
2017-10-11 | 14XX N. Oakley Blvd. |  |  | 12 | 17 | 12 | 5.0
2017-10-27 | 14XX N. Oakley Blvd. |  |  | 42 | 31 | 14 | 6.1
2017-11-11 | 14XX N. Oakley Blvd. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-12-08 | 14XX N. Oakley Blvd. |  |  | 7.4 | 19 | 13 | 4.1
2017-08-29 | 14XX N ELK GROVE AVE |  |  | 1.7 | 7.5 | 3.7 | 2.1
2017-12-20 | 14XX N ELK GROVE AVE |  |  | 4.1 | 8.8 | 5.7 | 1.7 | 1.7
2016-10-26 | 1XX W. 70th St. | Site 1 |  | 1.6 | 1.8 | 1.9 | 0.7
2016-10-25 | 15XX S. St. Louis Ave. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-05-25 | 15XX S. St. Louis Ave. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-11-03 | 15XX N LAWLER AVE |  |  | 1.4 | 1.4 | 1.5 | 1.3
2017-11-16 | 15XX N LAWLER AVE |  |  | 2.1 | 0.9 | 0.9 | 1.0
2017-09-13 | 15XX N HONORE ST |  |  | 3.5 | 14 | 9.4 | 5.0
2016-10-26 | 1XX W. 70th St. | Site 2 |  | 0.9 | 0.8 | 1.5 | 0.6
2017-10-25 | 16XX N Normandy Ave. |  |  | 5.3 | 12 | 16 | 6.0 | 6.1
2017-11-13 | 16XX N Normandy Ave. |  |  | 19 | 17 | 21 | 6.6
2017-11-17 | 16XX N Normandy Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-12-08 | 16XX N Normandy Ave. |  |  | 10 | 17 | 21 | 6.8
2016-11-22 | 16XX W. 37th St. |  |  | 3.2 | 6.1 | 8.8 | 1.9
2017-06-23 | 18XX W. 34th St. | Site 1 |  | 1.8 | 3.5 | 4.2 | 2.3
2017-09-22 | 18XX W. 34th St. | Site 1 |  | 2.6 | 3.8 | 3.7 | 2.7
2017-06-23 | 18XX W. 34th St. | Site 2 |  | 3.3 | 3.5 | 5.9 | 2.3
2017-06-23 | 18XX W. 34th St. | Site 3 |  | 2.2 | 1.7 | 1.9 | 0.9
2017-09-15 | 18XX W. 34th St. | Site 3 |  | 2.6 | 2.3 | 2.4 | 2.4
2017-10-04 | 18XX W. 34th St. | Site 3 |  | 2.1 | 2.1 | 2.1 | 1.1 | 1.2
2017-11-01 | 18XX W. 34th St. | Site 3 |  | 1.5 | 1.6 | 1.7 | 0.9
2017-12-06 | 18XX W. 34th St. | Site 3 |  | 1.9 | 2.2 | 1.9 | 0.9
2017-06-23 | 18XX W. 34th St. | Site 4 |  | 2.6 | 1.0 | 1.2 | 0.9
2017-09-15 | 18XX W. 34th St. | Site 4 |  | 1.6 | 1.8 | 1.9 | 2.0
2017-11-14 | 19XX S CENTRAL PARK AVE |  |  | <0.3 | <0.3 | <0.3 | 9.2
2017-09-20 | 19XX W WINONA ST |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-12-21 | 19XX W WINONA ST |  |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-12-01 | 20XX W. Chase Ave. |  |  | 9.3 | 14 | 19 | 2.6
2018-01-05 | 20XX W. Chase Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-12-28 | 21XX W 68TH ST |  |  | 3.2 | 3.8 | 4.0 | 1.3
2016-09-08 | 21XX N. Springfield Ave. | Site 1 |  | 0.8 | 0.6 | 0.6 | 0.5
2016-11-02 | 21XX W. Agatite Ave. | Site 1 |  | 7.3 | 22 | 16 | 3.4
2017-01-18 | 21XX W. Agatite Ave. | Site 1 |  | 6.8 | 12 | 9.0 | 2.1
| 21XX W. Agatite Ave. | Site 1 |  | Customer was Non-Responsive
2016-09-07 | 21XX N. Springfield Ave. | Site 2 |  | 2.0 | 1.7 | 1.6 | 1.5
2017-01-11 | 21XX N. Springfield Ave. | Site 2 |  | 1.1 | 0.8 | 0.9 | 0.5
2017-02-08 | 21XX N. Springfield Ave. | Site 2 |  | 1.1 | 0.6 | 0.6 | 0.4
2017-03-13 | 21XX N. Springfield Ave. | Site 2 |  | 1.3 | 0.9 | 0.9 | 0.5
2017-04-04 | 21XX N. Springfield Ave. | Site 2 |  | 0.8 | 0.8 | 0.8 | 0.7
2017-05-03 | 21XX N. Springfield Ave. | Site 2 |  | 0.9 | 1.0 | 1.1 | 0.8
2017-06-07 | 21XX N. Springfield Ave. | Site 2 |  | 1.4 | 1.5 | 1.7 | 1.2 | 1.2
2017-03-23 | 21XX W. Grace St. |  |  | 5.2 | 4.3 | 4.0 | 2.7
2016-10-27 | 21XX W. Sunnyside Ave. | Site 1 |  | 4.3 | 5.5 | 6.4 | 3.8
2017-01-20 | 21XX W. Sunnyside Ave. | Site 1 |  | 3.0 | 4.2 | 7.9 | 5.0
2016-11-03 | 21XX N. Maplewood Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-03-15 | 21XX N. Maplewood Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-06-08 | 21XX W. 54th Pl. |  |  | 1.8 | 1.8 | 2.6 | 1.0
2016-10-27 | 21XX N. Maplewood Ave. | Site 2 |  | 4.3 | 5.6 | 5.3 | 4.1
2017-03-15 | 21XX N. Maplewood Ave. | Site 2 |  | 4.2 | 6.5 | 5.8 | 2.5
2016-10-27 | 21XX W. Agatite Ave. | Site 2 |  | 1.7 | 2.2 | 1.9 | 1.0 | 0.9
2017-01-18 | 21XX W. Agatite Ave. | Site 2 |  | 1.1 | 1.0 | 1.0 | 0.5
2016-09-08 | 21XX N. Avers Ave. |  |  | 6.8 | 10 | 11 | 7.4
2017-01-11 | 21XX N. Avers Ave. |  |  | 6.0 | 8.8 | 12 | 8.7
2016-11-03 | 21XX N. Maplewood Ave. | Site 3 |  | 2.2 | 0.7 | 0.7 | 0.6
2017-03-16 | 21XX N. Maplewood Ave. | Site 3 |  | 0.7 | 0.7 | 1.6 | 0.7
2016-10-27 | 21XX W. Sunnyside Ave. | Site 2 |  | 4.8 | 5.1 | 9.1 | 4.2
2017-01-20 | 21XX W. Sunnyside Ave. | Site 2 |  | 2.1 | 4.0 | 7.3 | 2.2
2016-10-27 | 22XX N. Maplewood Ave. |  |  | 3.2 | 11 | 7.3 | 3.2
2017-03-15 | 22XX N. Maplewood Ave. |  |  | 2.7 | 2.9 | 2.4 | 1.6
2017-04-12 | 22XX N. Maplewood Ave. |  |  | 4.2 | 10 | 6.2 | 2.1
2017-05-17 | 22XX N. Maplewood Ave. |  |  | 4.5 | 12 | 7.9 | 2.8
2017-06-21 | 22XX N. Maplewood Ave. |  |  | 3.8 | 13 | 8.5 | 3.4
2017-07-12 | 22XX N. Maplewood Ave. |  |  | 3.8 | 11 | 8.2 | 3.7
2017-08-16 | 22XX N. Maplewood Ave. |  |  | 5.3 | 11 | 8.0 | 4.5
2016-10-27 | 23XX N. Maplewood Ave. |  |  | 2.8 | 5.7 | 6.1 | 2.8
2017-03-21 | 23XX N. Maplewood Ave. |  |  | 2.7 | 7.2 | 7.8 | 1.5
2016-09-15 | 23XX W. Jarvis Ave. |  |  | 6.1 | 10 | 3.1 | 1.8
2016-12-21 | 23XX W. Jarvis Ave. |  |  | 5.3 | 5.3 | 7.4 | 1.2 | 1.3
2017-03-28 | 24XX N. Talman Ave. | Site 1 |  | 8.6 | 23 | 18 | 4.6
2017-07-18 | 24XX N. Talman Ave. | Site 1 |  | 14 | 26 | 20 | 7.7
| 24XX N. Talman Ave. | Site 1 |  | Customer Declined Further Testing
2017-03-22 | 24XX N. Francisco Ave. | Site 1 |  | 2.8 | 6.3 | 4.5 | 1.4
2017-07-11 | 24XX N. Francisco Ave. | Site 1 |  | 4.9 | 8.5 | 6.3 | 3.1
2017-08-23 | 24XX N. Francisco Ave. | Site 1 |  | 4.7 | 6.7 | 6.8 | 9.2
2017-09-26 | 24XX N. Francisco Ave. | Site 1 |  | 3.3 | 3.5 | 5.4 | 2.8
2017-10-18 | 24XX N. Francisco Ave. | Site 1 |  | 4.4 | 5.9 | 6.2 | 2.8 | 2.8
2017-11-15 | 24XX N. Francisco Ave. | Site 1 |  | 8.3 | 5.9 | 7.5 | 2.2
2017-12-13 | 24XX N. Francisco Ave. | Site 1 |  | 4.4 | 10 | 7.2 | 2.0
2017-04-03 | 24XX N. Francisco AVE | Site 2 |  | 7 | 37 | 37 | 4.9
2017-07-11 | 24XX N. Francisco AVE | Site 2 |  | 9.4 | 11 | 9.8 | 4.2 | 4
| 24XX N. Francisco AVE | Site 2 |  | Customer Declined Further Testing
2017-10-04 | 24XX N CAMPBELL AVE | Site 1 |  | <0.3 | <0.3 | <0.3 | 11
2017-10-18 | 24XX N CAMPBELL AVE | Site 1 |  | <0.3 | <0.3 | <0.3 | 12
2017-10-25 | 24XX N CAMPBELL AVE | Site 1 |  | <0.3 | <0.3 | <0.3 | 9.8
2017-04-03 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-07-18 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-16 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-09-29 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-10-25 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-11-13 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-12-13 | 24XX N. Francisco Ave. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-07 | 24XX N. Talman Ave. | Site 2 |  | 4.2 | 1.3 | 1.3 | 1.1
2017-09-25 | 24XX N CAMPBELL AVE | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-06 | 24XX N. Talman Ave. | Site 3 |  | 5.1 | 11 | 9.7 | 1.9 | 1.9
2017-07-18 | 24XX N. Talman Ave. | Site 3 |  | 4.4 | 7.7 | 9.5 | 3.2
2017-09-21 | 24XX N CAMPBELL AVE | Site 3 |  | 2.3 | 2.4 | 1.8 | 1.3
2017-03-16 | 24XX N. Hamlin Ave.** |  |  | 15 | 3.8 | 4.1 | 1.8
2017-04-04 | 24XX N. Hamlin Ave.** |  |  | See Follow-Up Sequential Sampling Table for Results
2017-04-18 | 24XX N. Hamlin Ave.** |  |  | 25 | 19 | 270 | 2.9
2017-04-06 | 25XX N. Washtenaw Ave. |  |  | 2.1 | 2.2 | 1.8 | 1.4
2017-07-19 | 25XX N. Washtenaw Ave. |  |  | 2.4 | 2.9 | 2.8 | 2.6
2017-04-19 | 25XX N. Talman Ave. |  |  | 0.8 | 0.7 | 0.9 | 0.5 | 0.5
2017-07-19 | 25XX N. Talman Ave. |  |  | 0.6 | 0.8 | 0.8 | 0.7
2017-09-21 | 25XX N CAMPBELL AVE |  |  | <0.3 | <0.3 | <0.3 | <0.3
2016-10-19 | 25XX N. Keeler Ave. |  |  | 3.6 | 5.3 | 25 | 7.0
2016-11-02 | 25XX N. Keeler Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-05-17 | 25XX N. Keeler Ave. |  |  | 4.2 | 6.0 | 20 | 3.2
2016-11-03 | 25XX W. Shakespeare Ave. |  |  | 2.8 | 2.5 | 4.4 | 1.6
2017-03-14 | 25XX W. Shakespeare Ave. |  |  | 1.7 | 1.3 | 1.7 | 0.9
2017-04-12 | 25XX W. Shakespeare Ave. |  |  | 1.6 | 1.6 | 2.7 | 1.1 | 1.2
2017-05-17 | 25XX W. Shakespeare Ave. |  |  | 1.6 | 1.4 | 1.9 | 1.4
2017-06-14 | 25XX W. Shakespeare Ave. |  |  | 1.4 | 1.4 | 1.5 | 1.3
2017-07-12 | 25XX W. Shakespeare Ave. |  |  | 1.7 | 1.2 | 1.7 | 1.7
2017-08-16 | 25XX W. Shakespeare Ave. |  |  | 1.8 | 1.7 | 1.9 | 1.9
2017-03-28 | 26XX W. Homer St. |  |  | 13 | 3.4 | 2.9 | 1.8
2017-04-12 | 26XX W. Homer St. |  |  | 4.1 | 7.0 | 7.0 | 2.0
2017-05-18 | 26XX N. Whipple St. |  |  | 1.9 | 5.5 | 4.3 | 1.8
2017-08-04 | 26XX N. Whipple St. |  |  | 1.9 | 4.9 | 3.9 | 2.2
2017-03-28 | 26XX W. Altgeld St. |  |  | 2.2 | 2.2 | 1.3 | 0.7
2017-07-21 | 26XX W. Altgeld St. |  |  | 4.2 | 4.4 | 2.4 | 1.5
2017-06-19 | 26XX N. Drake Ave. | Site 1 |  | 5.9 | 5.9 | 4.9 | 4.0
2017-04-10 | 26XX W. Fullerton Ave. |  |  | 6.8 | 2.8 | 3.6 | 1.6 | 1.6
2017-07-19 | 26XX W. Fullerton Ave. |  |  | 5.1 | 2.7 | 3.3 | 2.1
2016-09-30 | 26XX S. Sacramento Ave. |  |  | 2.2 | 0.9 | 0.7 | 0.5 | 0.6
2017-02-10 | 26XX S. Sacramento Ave. |  |  | 1.3 | <0.3 | <0.3 | <0.3
2017-06-19 | 26XX N. Drake Ave. | Site 2ˆ |  | 4.6 | 22 | 16 | 5.6
2017-08-04 | 26XX N. Drake Ave. | Site 2ˆ |  | See Follow-Up Sequential Sampling Table for Results
2017-10-10 | 2XX W 107TH ST |  |  | 3.0 | 3.7 | 4.1 | 3.2
2017-06-19 | 27XX N. Drake Ave. | Site 1 |  | 14 | 10 | 10 | 3.1
2017-08-15 | 27XX N. Drake Ave. | Site 1 |  | 7.5 | 7.2 | 7.1 | 4.0
2017-05-18 | 27XX N. Whipple St. | Site 2 |  | 1.5 | 1.4 | 2.0 | 0.9
2017-08-11 | 27XX N. Whipple St. | Site 2 |  | 1.4 | 1.6 | 1.8 | 1.4
2017-09-13 | 27XX N. Whipple St. | Site 2 |  | 1.2 | 1.2 | 1.3 | 1.3
2017-10-11 | 27XX N. Whipple St. | Site 2 |  | 1.0 | 0.9 | 0.8 | 1.0
2017-11-15 | 27XX N. Whipple St. | Site 2 |  | 0.8 | 0.6 | 0.5 | 0.6
2017-12-13 | 27XX N. Whipple St. | Site 2 |  | 0.5 | 0.4 | 0.4 | 0.4
2017-05-19 | 27XX N. Whipple St. | Site 3 |  | 2.9 | 3.7 | 7.4 | 1.7
2017-08-04 | 27XX N. Whipple St. | Site 3 |  | 3.7 | 4.4 | 8.2 | 2.5
2017-09-06 | 27XX N. Whipple St. | Site 4 |  | 12 | 14 | 13 | 4.4
2017-10-11 | 27XX N. Whipple St. | Site 4 |  | 9.2 | 12 | 10 | 3.6 | 3.5
2017-11-15 | 27XX N. Whipple St. | Site 4 |  | 10 | 13 | 9.7 | 2.5
2017-12-13 | 27XX N. Whipple St. | Site 4 |  | 11 | 13 | 10 | 2.2
2017-05-18 | 27XX N. Whipple St. | Site 4 |  | 13 | 14 | 13 | 3.1
2017-08-04 | 27XX N. Whipple St. | Site 4 |  | 13 | 15 | 13 | 4.8
| 27XX N. Whipple St. | Site 4 |  | Customer Declined Further Testing
2017-05-19 | 27XX N. Whipple St. | Site 5 |  | 1.0 | 1.4 | 1.5 | 2.9
2017-08-25 | 27XX N. Whipple St. | Site 5 |  | 1.0 | 1.4 | 1.3 | 3.0
2017-05-19 | 27XX N. Whipple St. | Site 6 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-03 | 27XX N. Whipple St. | Site 6 |  | <0.3 | <0.3 | <0.3 | 0.5
2017-06-19 | 27XX N. Drake Ave. | Site 2 |  | 2.0 | 0.9 | 0.8 | 1.5
2017-08-11 | 27XX N. Drake Ave. | Site 2 |  | 1.6 | 1.5 | 1.8 | 2.2
2017-09-06 | 27XX N. Drake Ave. | Site 2 |  | 1.8 | 2.6 | 3.5 | 1.7
2017-10-11 | 27XX N. Drake Ave. | Site 2 |  | 1.9 | 1.5 | 1.2 | 1.5
2017-11-15 | 27XX N. Drake Ave. | Site 2 |  | 1.0 | 0.9 | 0.9 | 0.7
2017-12-13 | 27XX N. Drake Ave. | Site 2 |  | 1.8 | 1.1 | 1.1 | 0.7
2017-05-30 | 27XX N. Whipple St. | Site 1 |  | 7.3 | 9.1 | 9.5 | 3.8
2017-08-08 | 27XX N. Whipple St. | Site 1 |  | 18 | 14 | 8.6 | 4.8 | 4.9
| 27XX N. Whipple St. | Site 1 |  | Customer Declined Further Testing
2016-09-30 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-03-22 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-12 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-05-17 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-06-14 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-07-12 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-16 | 28XX N. Christiana Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2016-09-30 | 28XX N. Christiana Ave. | Site 2 |  | 19 | 15 | 13 | 8.4
2017-03-15 | 28XX N. Christiana Ave. | Site 2 |  | 12 | 16 | 12 | 4.6
2017-04-07 | 28XX N. Christiana Ave. | Site 2 |  | See Follow-Up Sequential Sampling Table for Results
2016-10-25 | 28XX W. 40th St.** |  |  | 3.2 | 2.6 | 2.8 | 2.0
2017-02-24 | 28XX W. 40th St.** |  |  | 34 | 51 | 20 | 1.3
2017-03-03 | 28XX W. 40th St.** |  |  | See Follow-Up Sequential Sampling Table for Results
2016-09-30 | 28XX N. Christiana Ave. | Site 3 |  | 5.6 | 11 | 11 | 5.2
2017-03-15 | 28XX N. Christiana Ave. | Site 3 |  | 5.7 | 8.0 | 8.1 | 2.7
2016-10-19 | 29XX W. 40th St. |  |  | 4.5 | 4.9 | 4.1 | 2.7
2017-02-24 | 29XX W. 40th St. |  |  | 3.5 | 2.2 | 1.9 | 1.4
2017-10-25 | 29XX N MOBILE AVE |  |  | 8.5 | 8.4 | 8.6 | 3.6
2017-12-06 | 29XX N MOBILE AVE |  |  | 9.9 | 9.7 | 8.9 | 3.4
2017-07-26 | 29XX W. Wilson Ave. |  |  | 9.3 | 13 | 12 | 3.9
2017-12-12 | 29XX N GRESHAM AVE |  |  | 0.9 | 0.6 | 0.6 | 0.4
2017-12-22 | 30XX W 41ST ST |  |  | 3.6 | 6.8 | 6.6 | 1.8
2017-08-09 | 30XX W. Wilson Ave. |  |  | 1.7 | 3.8 | 6.1 | 1.8
2016-10-06 | 30XX W. Diversey Ave. | Site 1 |  | 7.8 | 8.3 | 12 | 5.3
2017-03-15 | 30XX W. Diversey Ave. | Site 1 |  | 5.5 | 7.0 | 8.0 | 3.0
2016-10-06 | 30XX W. Diversey Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-03-14 | 30XX W. Diversey Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-12 | 30XX W. Diversey Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-05-18 | 30XX W. Diversey Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-03-21 | 30XX S. Homan Ave. |  |  | 0.5 | 0.5 | 1.3 | <0.3
2017-06-22 | 30XX S. Homan Ave. |  |  | 0.7 | 0.7 | 1.7 | 0.5
2017-04-05 | 31XX N. Rutherford Ave. | Site 3 |  | 2.4 | 3.9 | 3.8 | 1.3
2017-06-29 | 31XX N. Ridgeway Ave. | Site 1 |  | 3.8 | 6.1 | 6.0 | 3.9
2017-08-18 | 31XX N. Ridgeway Ave. | Site 1 |  | 5.5 | 13 | 11 | 5.4
2017-10-11 | 31XX N. Ridgeway Ave. | Site 2 |  | 5.8 | 7.8 | 5.1 | 3.1
2017-11-15 | 31XX N. Ridgeway Ave. | Site 2 |  | 4.5 | 7.4 | 9.6 | 6.4
2017-12-06 | 31XX N. Ridgeway Ave. | Site 2 |  | 8.1 | 8.6 | 5.6 | 3.0
2017-06-21 | 31XX N. Ridgeway Ave. | Site 2 |  | 7.9 | 6.2 | 3.4 | 5.6 | 5.3
2017-08-18 | 31XX N. Ridgeway Ave. | Site 2 |  | 6.8 | 8.8 | 6.1 | 9.5
| 31XX N. Ridgeway Ave. | Site 2 |  | Customer Declined Further Testing
2016-09-07 | 32XX W Thomas St. |  |  | 10 | 25 | 73 | 9.8
2017-08-02 | 32XX W Thomas St. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-10-30 | 32XX N NATCHEZ AVE |  |  | 2.2 | 2.4 | 4.1 | 2.2
2017-04-10 | 32XX N. Nagle Ave. | Site 1 |  | 4.9 | 6.6 | 6.7 | 3.4
2017-06-27 | 32XX N. Nagle Ave. | Site 1 |  | 3.7 | 6.6 | 8.1 | 6.0
2017-08-24 | 32XX N. Nagle Ave. | Site 1 |  | 4.6 | 7.1 | 8.2 | 6.0
2017-09-21 | 32XX N. Nagle Ave. | Site 1 |  | 4.7 | 7.2 | 7.4 | 5.5
2017-10-19 | 32XX N. Nagle Ave. | Site 1 |  | 4.1 | 8.0 | 8.3 | 5.5
2017-11-16 | 32XX N. Nagle Ave. | Site 1 |  | 4.6 | 7.4 | 7.7 | 7.8
2017-12-08 | 32XX N. Nagle Ave. | Site 1 |  | 5.0 | 10 | 8.3 | 7.2
2017-04-07 | 32XX N. Nagle Ave. | Site 2 |  | 0.5 | 0.6 | 0.6 | 0.5
2017-06-28 | 32XX N. Nagle Ave. | Site 2 |  | 2.0 | 2.4 | 2.2 | 1.3 | 1.3
2016-09-30 | 32XX W. Diversey Ave. |  |  | 4.5 | 6.2 | 4.5 | 2.0
2017-03-14 | 32XX W. Diversey Ave. |  |  | 1.4 | 1.8 | 2.4 | 1.6
2017-04-13 | 32XX W. Diversey Ave. |  |  | 1.4 | 1.7 | 2.2 | 1.4
2017-05-17 | 32XX W. Diversey Ave. |  |  | 3.1 | 6.1 | 3.3 | 1.2
2017-06-14 | 32XX W. Diversey Ave. |  |  | 1.7 | 4.6 | 7.1 | 1.6
2017-07-12 | 32XX W. Diversey Ave. |  |  | 2.1 | 2.0 | 2.1 | 1.7
2017-08-16 | 32XX W. Diversey Ave. |  |  | 2.9 | 6.9 | 5.9 | 2.1
2017-04-06 | 32XX N. Nagle Ave. | Site 3 |  | 2.9 | 6.1 | 7.3 | 2.2
2017-06-27 | 32XX N. Nagle Ave. | Site 3 |  | 4.5 | 5.6 | 11 | 7.6
2017-07-27 | 32XX N. Nagle Ave. | Site 3 |  | 7.2 | 5.0 | 7.1 | 5.1
2017-09-19 | 32XX N. Nagle Ave. | Site 3 |  | See Follow-Up Sequential Sampling Table for Results
2017-09-21 | 32XX N. Nagle Ave. | Site 3 |  | 8.1 | 9.8 | 12 | 4.6
2017-10-19 | 32XX N. Nagle Ave. | Site 3 |  | 3.7 | 7.5 | 11 | 4.0
2017-11-15 | 32XX N. Nagle Ave. | Site 3 |  | 4.2 | 7.1 | 10 | 3.0
2017-03-23 | 33XX N. Neva Ave. |  |  | 1.7 | 3.0 | 3.0 | 0.6
2017-04-10 | 33XX N. Neva Ave. |  |  | 2.7 | 3.5 | 2.6 | 1.0
2017-08-02 | 33XX W. 59th St. | Site 1 |  | 1.2 | 1.2 | 1.4 | 0.9
2017-08-10 | 33XX W. 59th St. | Site 2 |  | 0.7 | 0.6 | 0.8 | 0.4
2017-08-15 | 33XX W. 55th St. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-06 | 33XX N. Nagle Ave. |  |  | 2.0 | 2.2 | 2.2 | 1.0
2017-07-06 | 34XX S. Marshfield Ave. | Site 1 |  | 5.8 | 9.6 | 8.1 | 2.8 | 2.6
2016-10-25 | 34XX W. 12th Pl. | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-06-22 | 34XX S. Marshfield Ave. | Site 2 |  | 9.0 | 21 | 20 | 8.2
2017-07-10 | 34XX S. Marshfield Ave. | Site 2 |  | See Follow-Up Sequential Sampling Table for Results
2017-09-15 | 34XX S. Marshfield Ave. | Site 2 |  | 8.4 | 21 | 21 | 11
2017-10-13 | 34XX S. Marshfield Ave. | Site 2 |  | 8.1 | 21 | 21 | 8.7
2017-11-01 | 34XX S. Marshfield Ave. | Site 2 |  | 7.3 | 18 | 17 | 6.4
2017-12-06 | 34XX S. Marshfield Ave. | Site 2 |  | 9.5 | 18 | 25 | 6.5
2017-06-02 | 34XX N. Kostner Ave. | Site 1 |  | 1.6 | 1.9 | 2.1 | 0.9
2017-09-07 | 34XX N. Kostner Ave. | Site 1 |  | 2.2 | 3.4 | 4.5 | 1.7
2017-10-09 | 34XX N. Kostner Ave. | Site 1 |  | 1.9 | 4.5 | 3.0 | 1.3
2017-06-02 | 34XX N. Kostner Ave. | Site 2 |  | 4.2 | 4.4 | 4.0 | 2.1
2017-08-31 | 34XX N. Kostner Ave. | Site 2 |  | 4.4 | 6.5 | 7.6 | 3.2 | 3.1
2016-10-25 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-05-19 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-06-29 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-10 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-30 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-09-29 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-10-31 | 34XX W. 12th Pl. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-06-28 | 34XX S. Marshfield Ave. | Site 3 |  | 7.7 | 6.4 | 5.4 | 3.2
2017-10-04 | 34XX S. Marshfield Ave. | Site 3 |  | 17 | 5.1 | 4.4 | 3.6
2017-09-15 | 34XX S. Marshfield Ave. | Site 3 |  | 10 | 6.0 | 5.4 | 4.7
2017-11-01 | 34XX S. Marshfield Ave. | Site 3 |  | 6.7 | 5.0 | 4.5 | 3.2
2017-12-06 | 34XX S. Marshfield Ave. | Site 3 |  | 7.4 | 6.1 | 5.1 | 3.4
| 34XX S. Marshfield Ave. | Site 3 |  | Customer Declined Further Testing
2017-06-02 | 34XX N. Kostner Ave. | Site 3 |  | 3.3 | 5.8 | 8.5 | 1.7
2017-08-31 | 34XX N. Kostner Ave. | Site 3 |  | 3.5 | 5.0 | 7.9 | 2.7
2017-06-02 | 34XX N. Kostner Ave. | Site 4 |  | 10 | 2.0 | 9.9 | 0.9 | 0.9
2017-09-01 | 34XX N. Kostner Ave. | Site 4 |  | 11 | 3.3 | 3.5 | 1.0
2017-04-10 | 35XX N. Nagle Ave. | Site 1 |  | 1.8 | 4.3 | 3.2 | 0.9
2016-10-31 | 35XX W. 12th Pl. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-05-25 | 35XX W. 12th Pl. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-07 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-06-27 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-07-27 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-24 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-09-21 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-10-19 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-11-16 | 35XX N. Nagle Ave. | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2016-11-30 | 35XX S. Paulina St. |  |  | 0.8 | <0.3 | <0.3 | <0.3
2017-03-23 | 35XX S. Paulina St. |  |  | 0.5 | <0.3 | <0.3 | <0.3
2016-10-26 | 36XX W. 57th Pl. | Site 1 |  | 2.8 | 4.9 | 7.5 | 2.1
2017-03-21 | 36XX W. 57th Pl. | Site 1 |  | 14 | 1.8 | 2.3 | 0.9
2016-10-26 | 36XX W. 57th Pl. | Site 2 |  | 2.1 | 3.5 | 2.9 | 1.9
2017-03-17 | 36XX W. 57th Pl. | Site 2 |  | 2.3 | 3.2 | 3.4 | 1.3
2017-04-13 | 36XX W. 57th Pl. | Site 2 |  | 2.7 | 3.5 | 3.6 | 1.4
2017-05-18 | 36XX W. 57th Pl. | Site 2 |  | 3.2 | 7.8 | 6.7 | 2.0
2017-06-22 | 36XX W. 57th Pl. | Site 2 |  | 4.0 | 5.6 | 9.0 | 2.9
2017-07-20 | 36XX W. 57th Pl. | Site 2 |  | 3.3 | 4.9 | 7.3 | 2.8
2017-08-17 | 36XX W. 57th Pl. | Site 2 |  | 5.4 | 9.0 | 8.7 | 3.6
2016-11-22 | 36XX S. Paulina St. | Site 1 |  | 2.9 | 0.8 | 0.7 | 0.6
2017-03-10 | 36XX S. Paulina St. | Site 1 |  | 1.1 | 0.5 | 0.5 | 0.4
2017-04-13 | 36XX S. Paulina St. | Site 1 |  | 3.3 | 0.7 | 0.7 | 0.5
2016-10-26 | 36XX W. 57th Pl. | Site 3 |  | <0.3 | <0.3 | 0.3 | 0.3
2016-11-22 | 36XX S. Paulina St. | Site 2 |  | 2.7 | 4.4 | 4.5 | 2.3
2017-03-10 | 36XX S. Paulina St. | Site 2 |  | 4.6 | 10 | 6.6 | 1.8
2017-04-13 | 36XX S. Paulina St. | Site 2 |  | 9.1 | 8.9 | 4.7 | 2.1
2017-05-23 | 36XX S. Paulina St. | Site 2 |  | 270 | 12 | 7.9 | 2.9
2017-06-07 | 36XX S. Paulina St. | Site 2 |  | See Follow-Up Sequential Sampling Table for Results
2017-06-15 | 36XX S. Paulina St. | Site 2 |  | 4.1 | 4.7 | 4.8 | 3.1 | 3.2
2017-07-13 | 36XX S. Paulina St. | Site 2 |  | 3.8 | 6.2 | 7.4 | 3.0
2017-08-17 | 36XX S. Paulina St. | Site 2 |  | 4 | 4.6 | 4.4 | 3.5
2017-05-11 | 36XX N. Drake Ave. |  |  | 2.4 | 1.8 | 1.7 | 2.0
2017-08-24 | 36XX N. Drake Ave. |  |  | 2.0 | 4.0 | 4.2 | 2.4
2017-09-12 | 36XX N. Drake Ave. |  |  | 2.4 | 4.6 | 5.1 | 5.0
2017-10-11 | 36XX N. Drake Ave. |  |  | 6.1 | 2.1 | 2.0 | 1.9
2017-11-15 | 36XX N. Drake Ave. |  |  | 3.6 | 1.1 | 1.0 | 1.0 | 0.9
2017-12-13 | 36XX N. Drake Ave. |  |  | 2.9 | 1.0 | 0.8 | 0.8
2016-11-22 | 36XX S. Paulina St. | Site 3 |  | 2.2 | 3.1 | 2.1 | 1.8
2017-03-10 | 36XX S. Paulina St. | Site 3 |  | 3.3 | 3.4 | 2.3 | 1.8
2017-05-09 | 36XX N. Whipple St. |  |  | 1.2 | 2.1 | 2.4 | 1.1
2017-09-20 | 36XX N. Whipple St. |  |  | 2.9 | 2.9 | 3.0 | 2.4
2017-05-04 | 37XX N. Whipple St. | Site 6 |  | 2.1 | 1.9 | 1.5 | 1.0
2017-09-22 | 37XX N. Whipple St. | Site 6 |  | 5.1 | 5.3 | 4.0 | 2.2
2017-05-11 | 37XX N. Drake Ave. | Site 1 |  | 0.7 | 2.1 | 2.2 | 0.6
2017-08-24 | 37XX N. Drake Ave. | Site 1 |  | 1.2 | 2.0 | 2.2 | 1.2
2017-12-07 | 37XX N GREENVIEW AVE | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-04-25 | 37XX S. Michigan Ave. |  |  | 3.5 | 5.3 | 4.8 | 1.5
2016-10-26 | 37XX W. 57th Pl. | Site 1 |  | 0.8 | 0.4 | 0.5 | 0.4
2017-03-17 | 37XX W. 57th Pl. | Site 1 |  | 0.7 | 1.1 | 0.5 | 0.5
2017-05-11 | 37XX N. Drake Ave. | Site 2 |  | 2.1 | 3.8 | 3.3 | 1.7
2017-08-24 | 37XX N. Drake Ave. | Site 2 |  | 4.4 | 6.0 | 4.9 | 4.4
2017-05-11 | 37XX N. Drake Ave. | Site 3 |  | 2.2 | 4.0 | 2.5 | 1.2
2017-08-24 | 37XX N. Drake Ave. | Site 3 |  | 2.9 | 6.3 | 4.3 | 2.5
2016-10-25 | 37XX W. Ferdinand St. |  |  | 5.9 | 5.5 | 4.8 | 3.3
2017-07-11 | 37XX W. Ferdinand St. |  |  | 6.1 | 5.2 | 4.4 | 3.1
2017-08-23 | 37XX W. Ferdinand St. |  |  | 4.3 | 4.4 | 4.1 | 3.6 | 3.6
2017-12-06 | 37XX N GREENVIEW AVE | Site 2 |  | 4.1 | 8.0 | 6.7 | 2.1 | 2.1
2017-12-20 | 37XX N GREENVIEW AVE | Site 2 |  | <0.3 | <0.3 | <0.3 | 9.0
2017-05-10 | 37XX N. Drake Ave. | Site 4 |  | 0.9 | 1.1 | 1.2 | 0.7 | 0.7
2017-08-24 | 37XX N. Drake Ave. | Site 4 |  | 1.6 | 2.3 | 2.4 | 2.0
2017-10-06 | 37XX N WHIPPLE ST | Site 1 |  | 6.1 | 7.1 | 5.7 | 3.1
2017-05-05 | 37XX N. Whipple St. | Site 1 |  | 3.7 | 20 | 13 | 2.2
2017-05-27 | 37XX N. Whipple St. | Site 1 |  | See Follow-Up Sequential Sampling Table for Results
2016-10-26 | 37XX W. 57th Pl. | Site 2 |  | 0.5 | 0.5 | 0.7 | 0.7
2017-03-17 | 37XX W. 57th Pl. | Site 2 |  | 0.5 | 0.5 | 0.7 | 0.4
2017-05-09 | 37XX N. Whipple St. | Site 2 |  | 2.2 | 2.0 | 2.0 | 1.4 | 1.2
2017-09-19 | 37XX N. Whipple St. | Site 2 |  | 3.2 | 2.5 | 2.4 | 2.4
2017-10-25 | 37XX N. Whipple St. | Site 2 |  | 1.8 | 1.9 | 1.8 | 1.7
2017-11-09 | 37XX N. Whipple St. | Site 2 |  | 3.7 | 1.4 | 1.5 | 1.3 | 1.4
2017-12-07 | 37XX N. Whipple St. | Site 2 |  | 2.6 | 1.5 | 1.5 | 1.2
2017-06-13 | 37XX W. Eddy St. |  |  | 1.3 | 2.3 | 2.0 | 0.8
2017-07-13 | 37XX W. Eddy St. |  |  | 1.4 | 3.1 | 2.2 | 0.9
2017-05-05 | 37XX N. Whipple St. | Site 3 |  | 1.1 | 1.9 | 1.5 | 0.3
2017-09-19 | 37XX N. Whipple St. | Site 3 |  | 1.2 | 0.8 | 0.9 | 0.5
2017-10-05 | 37XX N. Whipple St. | Site 3 |  | 0.6 | 1.5 | 0.9 | 0.5
2017-11-02 | 37XX N. Whipple St. | Site 3 |  | 0.7 | 1.3 | 2.0 | 0.4
2017-12-12 | 37XX N. Whipple St. | Site 3 |  | 2.2 | 1.2 | 1.5 | 0.4
2017-05-05 | 37XX N. Whipple St. | Site 4 |  | 2.7 | 3.9 | 4.7 | 1.6
2017-09-19 | 37XX N. Whipple St. | Site 4 |  | 3.7 | 6.7 | 7.0 | 7.3
2017-05-04 | 37XX N. Whipple St. | Site 5 |  | 5.8 | 7.0 | 6.9 | 2.6
2017-09-22 | 37XX N. Whipple St. | Site 5 |  | 7.3 | 8.3 | 10 | 4.8
2017-10-05 | 37XX N. Whipple St. | Site 5 |  | 7.4 | 8.5 | 10 | 5.1
2017-11-02 | 37XX N. Whipple St. | Site 5 |  | 7.7 | 9.9 | 14 | 4.6 | 4.6
2017-12-07 | 37XX N. Whipple St. | Site 5 |  | 8.3 | 13 | 14 | 3.4
2017-04-04 | 38XX N. Kenneth Ave. |  |  | 1.9 | 2.7 | 1.9 | 0.9
2017-04-25 | 38XX N. Kenneth Ave. |  |  | 2.3 | 3.0 | 3.3 | 1.1
2017-05-04 | 38XX N. Whipple St. | Site 1 |  | 0.8 | 1.2 | 1.4 | 0.5
2017-09-20 | 38XX N. Whipple St. | Site 1 |  | 1.5 | 2.6 | 3.1 | 1.0
2017-05-09 | 38XX N. Whipple St. | Site 2 |  | 4.5 | 0.9 | 0.7 | 0.4
2017-09-20 | 38XX N. Whipple St. | Site 2 |  | 4.5 | 0.7 | 0.5 | 0.3
2017-10-05 | 38XX N. Whipple St. | Site 2 |  | 4.2 | 1.1 | 0.9 | 0.3
2017-11-02 | 38XX N. Whipple St. | Site 2 |  | 10 | 1.4 | 1.0 | <0.3
2017-05-09 | 38XX N. Whipple St. | Site 3 |  | 13 | 26 | 23 | 5.6
2017-05-27 | 38XX N. Whipple St. | Site 3 |  | See Follow-Up Sequential Sampling Table for Results
2017-08-10 | 38XX N. Whipple St. | Site 3 |  | See Follow-Up Sequential Sampling Table for Results
2017-09-28 | 38XX N. Whipple St. | Site 3 |  | 13 | 29 | 27 | 8.5
2017-05-10 | 38XX N. Drake Ave. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-08-23 | 38XX N. Drake Ave. |  |  | <0.3 | <0.3 | <0.3 | 0.3
2017-05-30 | 38XX N. Kedvale Ave. |  |  | 5.4 | 4.7 | 8.8 | 2.2
2017-09-28 | 38XX N. Kedvale Ave. |  |  | 7.0 | 8.4 | 11 | 4.4
2017-10-30 | 38XX N. Kedvale Ave. |  |  | 6.7 | 12 | 14 | 3.7
2017-11-28 | 38XX N. Kedvale Ave. |  |  | 6.0 | 5.0 | 8.9 | 2.7 | 2.7
2017-12-19 | 38XX N. Kedvale Ave. |  |  | 5.9 | 5.5 | 8.4 | 2.5
2017-11-20 | 38XX N ALTA VISTA TER. |  |  | 1.7 | 1.5 | 4.1 | 0.5 | 0.4
2017-05-04 | 39XX N. Whipple St. | Site 1 |  | 12 | 33 | 25 | 5.1
2017-06-07 | 39XX N. Whipple St. | Site 1 |  | See Follow-Up Sequential Sampling Table for Results
2017-09-26 | 39XX N. Whipple St. | Site 1 |  | 8.9 | 12 | 19 | 4.9
2017-05-05 | 39XX N. Whipple St. | Site 2 |  | 5.1 | 12 | 6.6 | 7.9
2017-09-22 | 39XX N. Whipple St. | Site 2 |  | 9.6 | 9.0 | 4.4 | 3.1
2017-05-05 | 39XX N. Whipple St. | Site 3 |  | 4.2 | 7.1 | 6.5 | 1.9
2016-11-02 | 39XX W. 57th Pl. |  |  | 1.6 | 3.3 | 3.3 | 1.6
2017-03-17 | 39XX W. 57th Pl. |  |  | 1.8 | 3.0 | 2.9 | 1.3
2017-07-07 | 40XX W. Carroll Ave. | Site 1 |  | 1.5 | 2.4 | 1.9 | 1.2
2017-09-29 | 40XX W. Carroll Ave. | Site 1 |  | 2.0 | 2.7 | 4.3 | 1.9
2017-10-20 | 40XX W. Carroll Ave. | Site 1 |  | 1.4 | 2.3 | 3.5 | 1.6
2017-11-28 | 40XX W. Carroll Ave. | Site 1 |  | 1.4 | 2.3 | 2.8 | 1.1
2017-12-15 | 40XX W. Carroll Ave. | Site 1 |  | 1.5 | 2.6 | 3.1 | 1.2
2017-07-06 | 40XX W. Carroll Ave. | Site 2 |  | 6.7 | 9.0 | 8.8 | 4.7
2017-09-29 | 40XX W. Carroll Ave. | Site 2 |  | 9.2 | 11 | 6.8 | 5.5 | 5.6
2017-10-20 | 40XX W. Carroll Ave. | Site 2 |  | 7.1 | 9.3 | 8.5 | 8.0 | 10
2017-11-17 | 40XX W. Carroll Ave. | Site 2 |  | 8.5 | 11 | 9.7 | 4.4
2017-12-15 | 40XX W. Carroll Ave. | Site 2 |  | 6.5 | 9.5 | 7.0 | 5.0
2017-10-06 | 41XX N DRAKE AVE |  |  | 0.4 | 0.7 | 1.0 | 0.6
2017-10-30 | 41XX N DRAKE AVE |  |  | 0.6 | 0.5 | 0.4 | 0.5
2017-06-02 | 41XX N. Troy St. |  |  | 1.2 | 2.5 | 2.5 | 1.7
2017-06-13 | 41XX N. Troy St. |  |  | 2.0 | 5.3 | 3.6 | 2.0
2017-06-21 | 41XX S. Michigan Ave. |  |  | 9.6 | 7.2 | 6.3 | 5.7
2017-10-25 | 41XX S. Michigan Ave. |  |  | 8.9 | 9.9 | 19 | 5.4
2017-11-22 | 41XX S. Michigan Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-12-07 | 41XX S. Michigan Ave. |  |  | 9.0 | 9.1 | 20 | 4.1
2016-09-29 | 4XX W. 103rd St. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-01-10 | 4XX W. 103rd St. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-10-19 | 41XX N HAMLIN AVE |  |  | 6.7 | 2.4 | 1.5 | 2.1
2017-10-30 | 41XX N LEAMINGTON AVE |  |  | 1.2 | 2.0 | 1.9 | 1.0
2017-11-13 | 41XX N LEAMINGTON AVE |  |  | 1.3 | 2.7 | 3.7 | 1.2
2016-09-29 | 4XX W. 101st Pl. | Site 1 |  | 1.3 | 2.5 | 2.3 | 1.1
2017-01-10 | 4XX W. 101st Pl. | Site 1 |  | 0.9 | 1.7 | 6.4 | 0.5
2017-02-08 | 4XX W. 101st Pl. | Site 1 |  | 1.0 | 2.3 | 1.8 | 0.6
2017-03-10 | 4XX W. 101st Pl. | Site 1 |  | 0.8 | 2.4 | 1.8 | 0.6
2017-04-04 | 4XX W. 101st Pl. | Site 1 |  | 1.0 | 1.9 | 1.8 | 0.6
2017-05-09 | 4XX W. 101st Pl. | Site 1 |  | 1.0 | 3.6 | 2.5 | 1.1
2017-06-06 | 4XX W. 101st Pl. | Site 1 |  | 1.2 | 3.6 | 2.5 | 1.1
2017-10-19 | 42XX N HAMLIN AVE | Site 1 |  | 4.3 | 8.1 | 6.7 | 2.6
2017-10-20 | 42XX N LAWNDALE AVE |  |  | 2.7 | 4.5 | 10 | 1.9
2017-10-19 | 42XX N HAMLIN AVE | Site 2 |  | 10 | 11 | 9.8 | 5.3
2017-10-20 | 42XX N HAMLIN AVE | Site 3 |  | 3.7 | 6.3 | 5.3 | 3.4
2017-06-21 | 42XX S. Indiana Ave. |  |  | 0.9 | 1.3 | 1.7 | 1.5
2017-10-24 | 42XX S. Indiana Ave. |  |  | 0.9 | 1.0 | 1.4 | 1.2 | 1.1
2017-10-19 | 42XX N. Hamlin Ave. |  |  | 5.8 | 21 | 17 | 8.1
2017-11-08 | 42XX N. Hamlin Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-11-22 | 42XX N HAMLIN AVE | Site 4 |  | 4.0 | 6.5 | 6.1 | 2.4
2016-09-29 | 4XX W. 101st Pl. | Site 2 |  | 3.5 | 5.8 | 7.2 | 3.1
2017-01-10 | 4XX W. 101st Pl. | Site 2 |  | 5.3 | 6.9 | 6.2 | 6.8
2017-02-22 | 42XX W. Hirsch St. |  |  | 1.1 | 0.6 | 0.7 | 0.5
2017-03-01 | 42XX W. Hirsch St. |  |  | 1.9 | 0.7 | 0.7 | 0.6
2017-10-20 | 42XX N HAMLIN AVE | Site 5 |  | 1.3 | 0.3 | <0.3 | <0.3
2017-11-01 | 4XX W 103RD ST |  |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2017-10-20 | 42XX N HAMLIN AVE | Site 6 |  | 2.4 | 2.3 | 1.8 | 1.5
2016-09-29 | 4XX W. 101st Pl. | Site 3 |  | 4.9 | 7.9 | 9.4 | 6.0
2017-01-11 | 4XX W. 101st Pl. | Site 3 |  | 6.2 | 8.4 | 7.6 | 2.8
2016-09-29 | 4XX W. 101st Pl. | Site 4 |  | 1.6 | 2.4 | 2.4 | 1.7
2017-01-11 | 4XX W. 101st Pl. | Site 4 |  | 2.6 | 2.3 | 4.2 | 1.6
2016-09-28 | 4XX W. 101st Pl. | Site 5 |  | 4.8 | 2.6 | 2.8 | 2.8
2017-10-19 | 43XX N HAMLIN AVE | Site 1 |  | 1.5 | 2.2 | 2.1 | 1.3
2017-11-17 | 43XX N MASON AVE |  |  | 1.1 | 1.4 | 1.6 | 0.9
2017-12-15 | 43XX N MASON AVE |  |  | 0.9 | 1.3 | 2.1 | 0.6
2017-04-26 | 43XX N. Campbell Ave. |  |  | 2.4 | 5.1 | 5.7 | 2.0
2017-05-10 | 43XX N. Campbell Ave. |  |  | 6.3 | 5.6 | 5.9 | 2.0
2017-10-27 | 43XX W SCHOOL ST |  |  | 4.0 | 5.2 | 5.4 | 3.6
2017-10-19 | 43XX N HAMLIN AVE | Site 2 |  | 0.5 | <0.3 | <0.3 | <0.3
2017-10-19 | 43XX N HAMLIN AVE | Site 3 |  | 2.5 | 4.8 | 3.5 | 2.2
2017-10-23 | 43XX N HAMLIN AVE | Site 4 |  | 6.0 | 7.1 | 8.1 | 3.6
2017-11-03 | 43XX W IRVING PARK RD |  |  | 1.0 | 0.8 | 0.7 | 0.6
2017-11-16 | 43XX W IRVING PARK RD |  |  | 1.0 | 0.8 | 0.8 | 0.6
2016-09-28 | 4XX W. 102nd St. |  |  | 3.3 | 4.2 | 3.6 | 2.9
2017-01-19 | 4XX W. 102nd St. |  |  | 2.6 | 3.0 | 3.1 | 0.9 | 0.9
2017-08-08 | 4XX W. 80th St. |  |  | 1.9 | 2.0 | 2.2 | 1.4
2016-09-28 | 4XX W. 101st Pl. | Site 6 |  | 1.8 | 1.5 | 1.9 | 1.1
2017-01-10 | 4XX W. 101st Pl. | Site 6 |  | 1.4 | 0.8 | 0.6 | 0.5
2016-09-28 | 4XX W. 101st Pl. | Site 7 |  | 0.9 | 2.1 | 2.2 | 1.0
2017-01-10 | 4XX W. 101st Pl. | Site 7 |  | 1.0 | 1.9 | 5.3 | 0.6
2016-10-27 | 44XX N. Hamilton Ave. |  |  | 1.7 | 1.9 | 1.8 | 1.1
2017-01-18 | 44XX N. Hamilton Ave. |  |  | 1.0 | 2.2 | 3.2 | 1.2
2017-08-09 | 44XX N. Sacramento Ave. | Site 1 |  | 4.5 | 6.7 | 6.3 | 4.3
2016-09-20 | 44XX N. Albany Ave. | Site 1 |  | 8.7 | 13 | 13 | 2.7
2017-01-04 | 44XX N. Albany Ave. | Site 1 |  | 6.2 | 2.7 | 2.9 | 1.1
2017-06-29 | 44XX S. Indiana Ave. | Site 1 |  | 1.7 | 2.2 | 2.4 | 2.3
2017-10-24 | 44XX S. Indiana Ave. | Site 1 |  | 1.9 | 2.9 | 3.0 | 2.0
2017-07-25 | 44XX N. Sacramento Ave. | Site 2 |  | 4.2 | 3.9 | 3.6 | 3.5
2017-06-21 | 44XX S. Indiana Ave. | Site 2 |  | 4.1 | 5.0 | 5.5 | 3.5
2017-10-24 | 44XX S. Indiana Ave. | Site 2 |  | 2.5 | 3.8 | 3.6 | 3.1
2017-08-09 | 44XX N. Sacramento Ave. | Site 3 |  | 8.6 | 7.5 | 9.2 | 6.1
2016-09-20 | 44XX N. Albany Ave. | Site 2 |  | 1.9 | 2.0 | 2.1 | 1.2
2017-07-25 | 44XX N. Whipple St. | Site 1 |  | 12 | 7.9 | 4.0 | 6.0
2017-08-17 | 44XX N. Sacramento Ave. | Site 4 |  | 2.4 | 3.3 | 5.1 | 2.3 | 2.3
2016-09-30 | 44XX N. Albany Ave. | Site 3 |  | 0.5 | 0.6 | 0.6 | 0.4
2017-01-04 | 44XX N. Albany Ave. | Site 3 |  | 1.2 | 1.1 | 1.5 | 0.5 | 0.5
2017-07-25 | 44XX N. Whipple St. | Site 2 |  | 6.9 | 10 | 8.6 | 3.0
2017-08-09 | 44XX N. Sacramento Ave. | Site 5 |  | 1.4 | 2.0 | 2.0 | 2.3
2016-09-07 | 44XX W. Grehaw St. |  |  | 8.2 | 6.5 | 3.5 | 2.3 | 2.3
2016-11-02 | 44XX W. Grehaw St. |  |  | 8.7 | 7.1 | 2.4 | 1.4
2017-10-24 | 44XX N MULLIGAN AVE |  |  | 3.6 | 7.0 | 9.6 | 14
2017-11-13 | 44XX N MULLIGAN AVE |  |  | 6.4 | 7.7 | 7.6 | 5.1
2017-07-25 | 45XX N. Sacramento Ave. | Site 1 |  | 0.8 | 0.8 | 0.8 | 0.7
2017-08-30 | 45XX N. Sacramento Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | 9.1
2017-09-13 | 45XX N. Sacramento Ave. | Site 1 |  | <0.3 | <0.3 | <0.3 | 9.3
2016-09-20 | 45XX N. Albany Ave. | Site 1 |  | 4.1 | 11 | 12 | 2.5
2017-01-04 | 45XX N. Albany Ave. | Site 1 |  | 2.3 | 3.1 | 3.2 | 1.9
2016-09-20 | 45XX N. Albany Ave. | Site 2 |  | 12 | 20 | 18 | 5.1
2016-10-29 | 45XX N. Albany Ave. | Site 2 |  | See Follow-Up Sequential Sampling Table for Results
2017-03-01 | 45XX N. Albany Ave. | Site 2 |  | 13 | 23 | 14 | 3.1
2017-04-19 | 45XX N. Albany Ave. | Site 2 |  | 34 | 43 | 29 | 4.4
2017-05-17 | 45XX N. Albany Ave. | Site 2 |  | 15 | 35 | 20 | 5.3
2017-06-14 | 45XX N. Albany Ave. | Site 2 |  | 14 | 25 | 18 | 5.0
2017-07-12 | 45XX N. Albany Ave. | Site 2 |  | 16 | 28 | 20 | 5.9 J | 12 J
2017-08-18 | 45XX N. Albany Ave. | Site 2 |  | 35 | 30 | 25 | 7.3
2017-10-20 | 45XX N SPAULDING AVE |  |  | 3.1 | 4.2 | 10 | 2.2
2017-12-20 | 45XX N SPAULDING AVE |  |  | 3.7 | 5.7 | 9.5 | 2.4
2017-07-26 | 45XX N. Sacramento Ave. | Site 2 |  | 2.5 | 7.1 | 7.4 | 2.3 | 2.2
2017-08-04 | 45XX N. Whipple St. | Site 4 |  | 5.9 | 26 | 19 | 6.1
2017-09-16 | 45XX N. Whipple St. | Site 4 |  | See Follow-Up Sequential Sampling Table for Results
2018-02-12 | 45XX N. Whipple St. | Site 4 |  | 8.6 | 5.1 | 4.4 | 3.2
2017-08-09 | 45XX N. Whipple St. | Site 1 |  | 1.0 | 1.1 | 1.0 | 0.5
2017-07-25 | 45XX N. Whipple St. | Site 2 |  | 2.9 | 2.3 | 1.9 | 1.2
2017-08-22 | 45XX N. Sacramento Ave. | Site 3 |  | 2.9 | 4.0 | 3.6 | 2.7
2017-08-04 | 45XX N. Sacramento Ave. | Site 4 |  | 1.7 | 3.6 | 6.4 | 1.8
2017-07-26 | 45XX N. Whipple St. | Site 3 |  | <0.3 | <0.3 | <0.3 | <0.3
2016-09-21 | 45XX N. Albany Ave. | Site 3 |  | 1.7 | 2.5 | 2.7 | 6.7 J | 4.1 J
2017-01-11 | 45XX N. Albany Ave. | Site 3 |  | 1.6 | 3.4 | 3.1 | 2.8
2017-08-17 | 45XX N. Sacramento Ave. | Site 5 |  | 8.3 | 7.4 | 7.0 | 3.0
2017-07-26 | 45XX N. Sacramento Ave. | Site 6 |  | 2.6 | 3.5 | 3.8 | 3.6
2017-12-01 | 46XX N LECLAIRE AVE |  |  | 2.0 | 2.2 | 2.9 | 1.0
2017-12-28 | 46XX N LECLAIRE AVE |  |  | 3.0 | 4.9 | 5.7 | 0.6
2017-07-28 | 47XX N. Sacramento Ave. | Site 1 |  | 1.7 | 2.1 | 2.0 | 1.4
2017-07-25 | 47XX N. Sacramento Ave. | Site 2 |  | 5.6 | 8.2 | 8.0 | 3.5
2017-09-06 | 48XX N MARRIMAC AVE |  |  | 2.6 | 1.7 | 2.9 | 2.2
2017-08-29 | 48XX N MARRIMAC AVE |  |  | 2.6 | 1.7 | 2.8 | 1.8
2017-10-23 | 48XX N MAGNOLIA AVE |  |  | 5.2 | 6.7 | 5.4 | 3.8
2017-04-05 | 48XX W. Eddy St. |  |  | 1.2 | 1.3 | 1.3 | 0.5
2017-04-18 | 48XX W. Eddy St. |  |  | 2.0 | 0.8 | 1.0 | 0.7
2017-10-20 | 49XX N GLENWOOD AVE |  |  | 4.5 | 5.4 | 6.2 | 1.6
2017-05-01 | 49XX W. Cortez St. |  |  | 9.0 | 3.0 | 2.7 | 2.4 | 2.4
2017-10-20 | 49XX N MAGNOLIA AVE | Site 1 |  | 2.5 | 2.6 | 5.8 | 1.6
2017-10-18 | 49XX N MAGNOLIA AVE | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3
2017-05-03 | 49XX W. Superior St. |  |  | 2.7 | 2.5 | 2.8 | 1.5
2017-04-24 | 49XX W. Walton St. |  |  | 0.4 | 0.5 | 0.6 | 0.3 | 0.3
2017-09-29 | 49XX W. Walton St. |  |  | 0.4 | 0.5 | 0.4 | 0.4
2017-04-25 | 50XX N. Neenah Ave. |  |  | 2.8 | 3.7 | 5.1 | 0.8
2017-05-10 | 50XX N. Neenah Ave. |  |  | 3.8 | 5.0 | 6.3 | 1.1
2017-09-20 | 50XX W BALMORAL AVE |  |  | 4.2 | 8.6 | 9.0 | 3.4 | 3.5
2017-10-13 | 50XX W BALMORAL AVE |  |  | 3.7 | 7.1 | 7.0 | 3.3
2017-09-20 | 50XX N WINCHESTER AVE |  |  | 8.7 | 22 | 20 | 8.6
2017-10-26 | 50XX N WINCHESTER AVE |  |  | See Follow-Up Sequential Sampling Table for Results
2017-12-04 | 50XX N WINCHESTER AVE |  |  | 5.9 | 7.6 | 5.7 | 3.8
2017-09-20 | 51XX N WINCHESTER AVE |  |  | 4.0 | 6.0 | 11 | 4.3
2017-11-30 | 51XX N WINCHESTER AVE |  |  | 3.7 | 4.4 | 4.4 | 2.2
2017-10-03 | 51XX S MORGAN ST |  |  | 1.2 | 2.7 | 3.2 | 1.4
2017-09-22 | 51XX S LONG AVE |  |  | 2.9 | 5.0 | 4.2 | 2.7
2017-10-12 | 51XX S LONG AVE |  |  | 3.1 | 5.9 | 4.4 | 2.6 | 2.5
2017-10-03 | 52XX S MORGAN ST | Site 1 |  | 6.0 | 9.1 | 8.1 | 5.7
2017-10-03 | 52XX S MORGAN ST | Site 2 |  | 0.6 | 1.0 | 0.9 | 0.9
2016-08-29 | 52XX W. Congress Pkwy. | Site 1 |  | 2.5 | 1.7 | 1.7 | 1.8
2016-08-31 | 52XX W. Congress Pkwy. | Site 2 |  | 5.5 | 5.3 | 5.1 | 3.9
2016-12-01 | 52XX W. Congress Pkwy. | Site 2 |  | 6.1 | 7.4 | 6.4 | 3.7
2016-08-30 | 52XX W. Congress Pkwy. | Site 3 |  | 2.7 | 1.2 | 1.1 | 0.8 | 0.8
2016-08-30 | 52XX W. Congress Pkwy. | Site 4 |  | 2.9 | 3.1 | 3.7 | 5.5
2017-03-16 | 53XX N. Bernard St.** |  |  | 3.8 | 3.3 | 3.0 | 2.6 | 2.6
2017-04-07 | 53XX N. Bernard St.** |  |  | 7.3 | 20 |  | 16
2017-04-29 | 53XX N. Bernard St.** |  |  | See Follow-Up Sequential Sampling Table for Results
2017-07-15 | 53XX N. Bernard St.** |  |  | See Follow-Up Sequential Sampling Table for Results
2016-08-29 | 53XX W. Congress Pkwy. | Site 1 |  | 4.3 | 6.4 | 6.0 | 3.9
2016-12-01 | 53XX W. Congress Pkwy. | Site 1 |  | 7.9 | 4.0 | 5.0 | 3.2
2016-08-31 | 53XX W. Congress Pkwy. | Site 2 |  | 3.8 | 9.9 | 8.0 | 3.4
2016-12-14 | 53XX W. Congress Pkwy. | Site 2 |  | 3.0 | 4.2 | 3.0 | 1.8
2017-11-09 | 53XX N LATROBE AVE |  |  | 1.0 | 0.6 | 0.7 | 0.4
2017-12-07 | 53XX N LATROBE AVE |  |  | 1.0 | 0.8 | 1.0 | 0.5
2016-08-30 | 53XX W. Congress Pkwy. | Site 3 |  | 2.1 | 2.2 | 2.6 | 1.9
2016-12-01 | 53XX W. Congress Pkwy. | Site 3 |  | 2.5 | 2.6 | 2.6 | 1.9
2017-09-20 | 53XX N LIEB AVE |  |  | 8.0 | 14 | 14 | 6.7
2017-10-13 | 53XX N LIEB AVE |  |  | 13 | 13 | 14 | 5.5
2017-12-08 | 53XX N LIEB AVE |  |  | 9.9 | 8.7 | 9.9 | 3.5
2017-10-13 | 53XX S MORGAN ST |  |  | 1.4 | 0.4 | 0.4 | 0.4
2016-08-30 | 53XX W. Congress Pkwy. | Site 4 |  | 2.4 | 1.2 | 1.2 | 1.0
2016-12-02 | 53XX W. Congress Pkwy. | Site 4 |  | 4.1 | 3.4 | 3.4 | 2.1 J | 1.3 J
2017-11-01 | 53XX S SPAULDING AVE |  |  | 3.4 | 6.9 | 7.3 | 2.1
2017-11-08 | 54XX S MORGAN ST | Site 1 |  | <0.3 | <0.3 | <0.3 | <0.3
2016-08-31 | 54XX W. Congress Pkwy. | Site 1 |  | 3.1 | 4.6 | 4.3 | 2.3
2016-12-02 | 54XX W. Congress Pkwy. | Site 1 |  | 2.9 | 3.9 | 3.6 | 2.7
2016-08-30 | 54XX W. Congress Pkwy. | Site 2 |  | 3.6 | 4.3 | 3.9 | 2.1
2016-12-02 | 54XX W. Congress Pkwy. | Site 2 |  | 4.4 | 4.7 | 6.0 | 2.1
2017-10-10 | 54XX N LOTUS AVE |  |  | 13 | 8.9 | 8.1 | 4.0
2017-10-23 | 54XX N LOTUS AVE |  |  | 5.3 | 3.9 | 4.0 | 2.7
2017-06-16 | 54XX S. Seeley Ave. | Site 2 |  | <0.3 | 0.3 | <0.3 | <0.3
2017-11-08 | 54XX S MORGAN ST | Site 2 |  | <0.3 | <0.3 | <0.3 | <0.3 | <0.3
2016-08-29 | 54XX W. Congress Pkwy. | Site 3 |  | 0.5 | 0.5 | 0.5 | 0.3
2016-12-01 | 54XX W. Congress Pkwy. | Site 3 |  | 1.2 | 0.8 | 0.6 | 0.4
2017-02-01 | 54XX W. Congress Pkwy. | Site 3 |  | 0.9 | 0.9 | 0.4 | 0.3 | 0.4
2017-03-01 | 54XX W. Congress Pkwy. | Site 3 |  | 0.9 | 0.7 | 0.4 | 0.4
2017-04-05 | 54XX W. Congress Pkwy. | Site 3 |  | 0.8 | 0.7 | 0.5 | 0.4 | 0.4
2017-05-03 | 54XX W. Congress Pkwy. | Site 3 |  | 0.8 | 0.8 | 0.5 | 0.4
2017-06-07 | 54XX W. Congress Pkwy. | Site 3 |  | 0.8 | 0.8 | 0.6 | 0.5
2017-06-08 | 54XX S. Hoyne Ave. |  |  | 3.6 | 5.5 | 6.6 | 2.0
2016-08-30 | 54XX W. Congress Pkwy. | Site 4 |  | 0.7 | 2.2 | 2.6 | 0.6
2016-12-06 | 54XX W. Congress Pkwy. | Site 4 |  | 1.0 | 1.2 | 1.2 | 0.7
2017-11-01 | 54XX S SPAULDING AVE |  |  | 3.1 | 1.8 | 1.9 | 1.5
2016-08-31 | 54XX W. Congress Pkwy. | Site 5 |  | 1.9 | 0.4 | 0.4 | 0.4
2017-06-07 | 54XX S. Seeley Ave. | Site 1 |  | 1.8 | 1.6 | 1.6 | 0.9
2017-08-01 | 56XX S. Christiana Ave. | Site 1 |  | 1.0 | 1.3 | 1.0 | 0.8
2017-08-01 | 56XX S. Christiana Ave. | Site 2 |  | 5.0 | 3.9 | 4.1 | 3.5
2017-08-02 | 56XX S. Christiana Ave. | Site 3 |  | 5.3 | 1.5 | 1.5 | 2.7
2017-08-02 | 56XX S. Christiana Ave. | Site 4 |  | 3.1 | 4.0 | 7.9 | 5.2
2017-08-01 | 57XX S. Christiana Ave. | Site 1 |  | 0.8 | 0.5 | 0.6 | 0.7
2017-09-18 | 57XX S CHRISTIANA AVE | Site 3 |  | 1.3 | 1.4 | 1.8 | 0.9 | 0.9
2017-08-01 | 57XX S. Christiana Ave. | Site 2 |  | 4.8 | 5.0 | 7.0 | 2.6 | 2.5
2017-08-31 | 57XX N MELVINA AVE |  |  | 1.8 | 1.6 | 1.8 | 1.1 | 1.1
2017-08-25 | 57XX S. Oak Park Ave. |  |  | 2.3 | 1.7 | 1.8 | 1.6
2017-08-25 | 57XX S. Oak Park Ave. |  |  | 2.3 | 1.7 | 1.8 | 1.6
2017-09-22 | 57XX S. Oak Park Ave. |  |  | 1.6 | 1.8 | 1.8 | 2.2
2017-04-19 | 57XX W. Midway Park | Site 1 |  | 1.5 | 1.9 | 3.6 | 2.4
2017-12-14 | 57XX W. Midway Park | Site 1 |  | 1.3 | 1.7 | 2.4 | 2.9 | 2.2
2017-12-13 | 57XX W. Race Ave. |  |  | 5.1 | 6.0 | 7.2 | 4.1 | 4.2
2017-04-26 | 57XX W. Race Ave. |  |  | 6.6 | 15 | 17 | 6.9
2017-05-17 | 57XX W. Race Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-04-19 | 57XX W. Midway Park | Site 2 |  | 1.8 | 2.5 | 2.5 | 1.0
2017-12-13 | 57XX W. Midway Park | Site 2 |  | 2.5 | 2.2 | 2.5 | 1.1
2017-10-23 | 58XX W BYRON ST |  |  | 0.6 | 1.3 | 1.9 | 0.9
2017-08-01 | 58XX S. Christiana Ave. |  |  | 3.8 | 3.3 | 7.8 | 3.0
2017-08-22 | 58XX S. Rutherford Ave. |  |  | 2.8 | 12 | 12 | 2.2
2017-09-07 | 58XX S. Rutherford Ave. |  |  | 8.6 | 11 | 10 | 2.3
2017-10-05 | 58XX S. Rutherford Ave. |  |  | 2.7 | 6.4 | 8.5 | 2.2 | 2.0
2017-11-02 | 58XX S. Rutherford Ave. |  |  | 2.7 | 8.7 | 14 | 2.1
2017-12-14 | 58XX S. Rutherford Ave. |  |  | 2.4 | 8.1 | 12 | 1.5
2017-06-05 | 59XX S. Campbell Ave. |  |  | 0.8 | 0.6 | 1.0 | 0.6
2017-06-12 | 60XX S. Campbell Ave. | Site 1 |  | 1.0 | 0.9 | 0.7 | 0.5
2017-01-17 | 60XX S. Moody Ave. |  |  | 0.8 | 0.6 | 0.7 | <0.3 | <0.3
2017-02-09 | 60XX S. Moody Ave. |  |  | 1.2 | 1.0 | 1.2 | 0.3
2017-06-06 | 60XX S. Campbell Ave. | Site 2 |  | 1.8 | 1.4 | 1.6 | 0.7
2017-04-13 | 60XX N. Leader Ave. |  |  | 5.3 | 8.2 | 12 | 2.2
2017-06-02 | 60XX N. Leader Ave. |  |  | 7.2 | 7.5 | 8.0 | 2.5
2017-06-05 | 60XX S. Campbell Ave. | Site 3 |  | 2.3 | 3.1 | 3.2 | 1.8 | 1.9
2017-02-13 | 60XX S. Kolin Ave. |  |  | 0.7 | 0.6 | 0.5 | 0.4
2017-03-08 | 60XX S. Kolin Ave. |  |  | 0.5 | <0.3 | <0.3 | <0.3
2017-06-05 | 60XX S. Campbell Ave. | Site 4 |  | 0.5 | 0.6 | 0.4 | <0.3
2017-06-05 | 60XX S. Campbell Ave. | Site 5 |  | 1.4 | 2.0 | 2.7 | 1.6
2017-06-05 | 60XX S. Campbell Ave. | Site 6 |  | 3.1 | 3.9 | 3.3 | 2.1
2017-06-12 | 61XXS. Campbell Ave. |  |  | 2.3 | 1.4 | 1.9 | 1.0
2017-02-02 | 61XX S. Moody Ave. |  |  | 1.2 | 2.5 | 2.7 | 1.5
2017-02-23 | 61XX S. Moody Ave. |  |  | 1.7 | 4.4 | 11 | 1.5
2017-10-25 | 61XX W LELAND AVE |  |  | 0.8 | 0.3 | 0.3 | 0.4
2017-11-16 | 61XX W LELAND AVE |  |  | 1.4 | 1.2 | 1.5 | 0.7
2017-09-25 | 62XX W GRAND AVE |  |  | 4.0 | 1.4 | 2.8 | 0.6 | 0.6
2017-10-09 | 62XX W GRAND AVE |  |  | 4.0 | 1.4 | 8.3 | 0.6
2017-06-05 | 62XX S. Campbell Ave. |  |  | 0.6 | <0.3 | <0.3 | <0.3
2017-05-04 | 62XX N. Kirkwood Ave. |  |  | 3.0 | 4.8 | 4.9 | 2.6
2017-05-31 | 62XX N. Kirkwood Ave. |  |  | 4.0 | 5.6 | 4.8 | 3.2
2017-04-04 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.3 | 1.5 | 1.5 | 0.8
2017-06-28 | 63XX S Kilpatrick Ave. | Site 1 |  | 3.7 | 2.0 | 1.8 | 1.5
2017-08-03 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.1 | 1.7 | 1.4 | 1.6
2017-08-17 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.3 | 2.1 | 2.1 | 1.6
2017-09-27 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.2 | 1.7 | 2.3 | 1.3
2017-10-30 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.2 | 1.7 | 2.2 | 1.0
2017-12-05 | 63XX S Kilpatrick Ave. | Site 1 |  | 1.3 | 1.9 | 2.1 | 0.9
2017-04-05 | 63XX S. Kilpatrick Ave. | Site 2 |  | 1.8 | 2.5 | 3.0 | 1.4
2017-06-27 | 63XX S. Kilpatrick Ave. | Site 2 |  | 2.6 | 3.9 | 3.4 | 2.7
2017-07-20 | 63XX S. Kilpatrick Ave. | Site 2 |  | 2.6 | 4.5 | 5.2 | 2.8
2017-08-25 | 63XX S. Kilpatrick Ave. | Site 2 |  | 2.2 | 4.0 | 4.6 | 2.8
2017-09-28 | 63XX S. Kilpatrick Ave. | Site 2 |  | 3.5 | 4.1 | 4.6 | 2.7
2017-10-24 | 63XX S. Kilpatrick Ave. | Site 2 |  | 2.0 | 3.9 | 5.1 | 2.0
2017-11-16 | 63XX S. Kilpatrick Ave. | Site 2 |  | 2.3 | 4.0 | 5.3 | 1.6 | 1.6
2017-04-11 | 64XX S. Kilpatrick Ave. |  |  | 4.5 | 13 | 13 | 2.6
2017-06-29 | 64XX S. Kilpatrick Ave. |  |  | 7.5 | 14 | 13 | 3.8
2017-05-31 | 64XX S. Maplewood Ave. |  |  | 1.5 | 1.4 | 1.5 | 0.9
2017-06-08 | 64XX S. Maplewood Ave. |  |  | 1.8 | 1.4 | 1.4 | 1.0
2017-11-03 | 6XX W 103RD ST |  |  | 0.6 | <0.3 | <0.3 | <0.3
2017-04-05 | 65XX S. Kilpatrick Ave. | Site 1 |  | 1.4 | 1.8 | 1.8 | 0.9 | 0.9
2017-06-28 | 65XX S. Kilpatrick Ave. | Site 1 |  | 2.3 | 2.6 | 2.8 | 1.5
2017-04-17 | 65XX S. Rockwell St. |  |  | 1.5 | 2.3 | 2.7 | 1.0
2017-04-19 | 65XX S. Maryland Ave. |  |  | 1.1 | 2.3 | 1.8 | 0.9
2017-08-22 | 65XX S. Maryland Ave. |  |  | 1.3 | 2.0 | 2.8 | 1.5
2017-09-26 | 65XX S. Maryland Ave. |  |  | 1.1 | 2.1 | 1.8 | 1.5 | 1.4
2017-10-17 | 65XX S. Maryland Ave. |  |  | 1.0 | 1.7 | 1.6 | 1.1
2017-11-17 | 65XX S. Maryland Ave. |  |  | 1.1 | 1.4 | 1.9 | 0.8
2017-12-19 | 65XX S. Maryland Ave. |  |  | 1.2 | 1.4 | 1.4 | 0.7
2017-04-11 | 65XX S. Kilpatrick Ave. | Site 2 |  | 2.7 | 3.3 | 2.3 | 1.5
2017-06-22 | 65XX S. Kilpatrick Ave. | Site 2 |  | 3.4 | 8.0 | 13 | 3.4
2017-04-06 | 65XX S. Kilpatrick Ave. | Site 3 |  | 4.1 | 5.4 | 4.1 | 1.0
2017-06-27 | 65XX S. Kilpatrick Ave. | Site 3 |  | 3.6 | 7.2 | 4.6 | 1.9
2017-04-06 | 66XX S. Kilpatrick Ave. | Site 1 |  | 1.5 | 1.3 | 0.9 | 0.5
2017-06-22 | 66XX S. Kilpatrick Ave. | Site 1 |  | 1.9 | 1.1 | 1.0 | 0.9
2017-04-05 | 66XX S. Kilpatrick Ave. | Site 2 |  | 1.8 | 1.7 | 1.9 | 1.6
2017-06-27 | 66XX S. Kilpatrick Ave. | Site 2 |  | 2.8 | 4.9 | 5.4 | 3.2
2017-09-27 | 66XX S. Kilpatrick Ave. | Site 3 |  | 2.1 | 2.8 | 3.0 | 1.8
2017-10-24 | 66XX S. Kilpatrick Ave. | Site 3 |  | 2.7 | 3.7 | 4.0 | 1.5
2017-11-16 | 66XX S. Kilpatrick Ave. | Site 3 |  | 2.4 | 3.9 | 4.0 | 1.2
2017-04-06 | 66XX S. Kilpatrick Ave. | Site 3 |  | 2.0 | 4.3 | 2.3 | 0.8
2017-06-22 | 66XX S. Kilpatrick Ave. | Site 3 |  | 4.0 | 5.8 | 8.4 | 5.0
2017-07-20 | 66XX S. Kilpatrick Ave. | Site 3 |  | 4.8 | 8.3 | 47 | 3.8
2017-08-25 | 66XX S. Kilpatrick Ave. | Site 3 |  | 6.5 | 6.2 | 9.5 | 2.6
2017-09-29 | 66XX S. Kilpatrick Ave. | Site 3 |  | See Follow-Up Sequential Sampling Table for Results
2017-04-05 | 66XX S. Kilpatrick Ave. | Site 4 |  | 2.6 | 3.8 | 7.5 | 1.8
2017-06-28 | 66XX S. Kilpatrick Ave. | Site 4 |  | 4.0 | 5.6 | 8.1 | 3.8
2017-07-28 | 66XX S. Kilpatrick Ave. | Site 4 |  | 2.6 | 3.0 | 4.6 | 2.5
2017-08-18 | 66XX S. Kilpatrick Ave. | Site 4 |  | 3.0 | 5.4 | 8.2 | 3.7
2017-09-27 | 66XX S. Kilpatrick Ave. | Site 4 |  | 2.7 | 2.1 | 2.7 | 2.3
2017-10-24 | 66XX S. Kilpatrick Ave. | Site 4 |  | 2.7 | 3.4 | 5.5 | 2.5
2017-11-16 | 66XX S. Kilpatrick Ave. | Site 4 |  | 2.9 | 4.2 | 13 | 2.1
2017-04-04 | 66XX S. Kilpatrick Ave. | Site 5 |  | 8.0 | 9.4 | 10 | 2.5
2017-06-27 | 66XX S. Kilpatrick Ave. | Site 5 |  | 10 | 11 | 12 | 8.3
2017-09-29 | 66XX N ODELL AVE |  |  | 4.0 | 6.3 | 5.3 | 3.4
2017-11-03 | 66XX N ODELL AVE |  |  | 3.7 | 5.0 | 6.5 | 2.9
2017-01-17 | 67XX W. 64th St. |  |  | 3.5 | 2.6 | 3.1 | 0.9
2017-02-13 | 67XX W. 64th St. |  |  | 8.0 | 3.3 | 3.0 | 1.1
2017-02-08 | 67XX N. Jean Ave. |  |  | 2.9 | 7.7 | 9.1 | 1.7
2017-05-16 | 67XX N. Jean Ave. |  |  | 6.0 | 19 | 23 | 2.9
2017-06-09 | 67XX N. Jean Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-06-13 | 67XX N. Jean Ave. |  |  | 2.6 | 12 | 15 | 2.6
2017-07-18 | 67XX N. Jean Ave. |  |  | 3.5 | 10 | 17 | 3.3
2017-08-18 | 67XX N. Jean Ave. |  |  | 5.4 | 16 | 23 | 3.7
2017-09-20 | 67XX N. Jean Ave. |  |  | 4.6 | 11 | 28 | 4.5
2017-10-13 | 67XX N. Jean Ave. |  |  | 4.4 | 11 | 21 | 3.9
2017-07-28 | 6824 S. Normal Blvd. |  |  | 3.1 | 5.8 | 4.6 | 3.3
2016-10-26 | 70XX S. Perry Ave. |  |  | 3.9 | 5.7 | 5.0 | 2.4 | 2.5
2017-04-11 | 71XX S. Honore St. | Site 1 |  | 2.2 | 4.6 | 6.5 | 1.0
2017-09-08 | 71XX S. Honore St. | Site 1 |  | 2.1 | 5.4 | 3.5 | 1.9
2017-04-11 | 71XX S. Honore St. | Site 2 |  | 0.9 | 0.9 | 1.0 | 0.5
2017-09-08 | 71XX S. Honore St. | Site 2 |  | 9.8 | 1.5 | 5.9 | 1.3 | 1.2
2017-05-31 | 71XX S. Rockwell St. |  |  | 2.7 | 3.1 | 3.0 | 2.4
2017-04-11 | 71XX S. Honore St. | Site 3 |  | 1.0 | 1.2 | 0.7 | 0.5
2017-09-08 | 71XX S. Honore St. | Site 3 |  | 1.4 | 1.4 | 2.2 | 1.5
2017-09-14 | 72XX S CRANDON AVE |  |  | <0.3 | 0.3 | 0.4 | <0.3
2017-10-12 | 72XX S CRANDON AVE |  |  | <0.3 | 1.0 | 0.4 | <0.3
2016-09-15 | 72XX N. Claremont Ave. |  |  | 2.6 | 5.3 | 5.5 | 3.7
2016-12-21 | 72XX N. Claremont Ave. |  |  | 2.5 | 6.8 | 8.1 | 1.8
2017-10-17 | 72XX W FITCH |  |  | 6.2 | 5.8 | 12 | 6.5
2017-11-07 | 72XX W FITCH |  |  | 4.5 | 5.6 | 9.4 | 7.5 J | 5.2 J
2017-05-31 | 72XX S. Rockwell St. |  |  | 1.4 | 2.9 | 3.4 | 1.4
2017-10-31 | 72XX S. Rockwell St. |  |  | 1.7 | 2.7 | 2.8 | 1.4 | 1.4
2017-04-25 | XX E. 37th Pl. |  |  | 4.1 | 5.8 | 3.5 | 0.8
2017-04-13 | 73XX S. Honore St. | Site 1 |  | 6.2 | 9.0 | 10 | 5.1
2017-04-11 | 73XX S. Honore St. | Site 2 |  | 3.1 | 4.5 | 4.0 | 1.3 | 1.3
2017-09-08 | 73XX S. Honore St. | Site 2 |  | 4.2 | 4.2 | 4.2 | 3.1
2017-05-31 | 73XX S. Rockwell St. | Site 1 |  | 2.9 | 2.3 | 2.9 | 2.1
2017-10-31 | 73XX S. Rockwell St. | Site 1 |  | 3.1 | 2.7 | 4.1 | 3.0
2017-12-05 | 73XX S. Rockwell St. | Site 1 |  | 4.5 | 5.0 | 5.4 | 2.1
2017-06-01 | 73XX S. Rockwell St. | Site 2 |  | 7.2 | 5.8 | 6.0 | 2.8
2017-10-31 | 73XX S ROCKWELL ST |  |  | 6.2 | 3.4 | 3.3 | 1.9
2017-01-17 | 74XX S. Calumet Ave. |  |  | 3.6 | 3.5 | 4.0 | 0.6
2017-02-14 | 74XX S. Calumet Ave. |  |  | 3.2 | 2.8 | 2.1 | 0.5 | 0.4
2017-12-12 | 77XX S WABASH AVE |  |  | 3.1 | 6.5 | 7.0 | 2.1
2017-12-21 | 77XX S WABASH AVE |  |  | 3.6 | 7.4 | 8.7 | 2.3
2017-09-28 | 78XX S MERRILL AVE |  |  | 3.0 | 5.4 | 7.5 | 3.4 | 3.4
2017-12-21 | 80XX S WABASH AVE |  |  | 1.4 | 0.7 | 1.4 | 0.4
2016-08-24 | 80XX S. Avalon Ave. |  |  | 4.0 | 3.8 | 3.7 | 2.4
2016-12-16 | 80XX S. Avalon Ave. |  |  | 2.9 | 2.0 | 2.0 | 1.0
2017-01-31 | 80XX S. Avalon Ave. |  |  | 3.6 | 4.0 | 4.0 | 1.1
2017-02-21 | 80XX S. Avalon Ave. |  |  | 3.2 | 2.4 | 2.2 | 1.0
2017-03-21 | 80XX S. Avalon Ave. |  |  | 2.7 | 2.1 | 2.1 | 1.1
2017-04-18 | 80XX S. Avalon Ave. |  |  | 2.7 | 2.7 | 2.4 | 1.2
2017-05-16 | 80XX S. Avalon Ave. |  |  | 3.6 | 5.3 | 4.3 | 2.1
2017-02-02 | 81XX S. Champlain Ave. |  |  | 7.4 | 7.1 | 8.0 | 2.9
2017-02-23 | 81XX S. Champlain Ave. |  |  | 10 | 4.9 | 7.6 | 3.9
2016-08-25 | 81XX S. Avalon Ave. |  |  | 1.1 | 1.4 | 1.3 | 1.1
2016-12-15 | 81XX S. Avalon Ave. |  |  | 0.7 | 1.1 | 1.0 | 0.4
2016-08-25 | 82XX S. Avalon Ave. | Site 1 |  | 2.1 | 1.0 | 0.7 | 0.7
2016-12-15 | 82XX S. Avalon Ave. | Site 1 |  | 1.2 | 1.3 | 0.8 | 0.7
2017-04-04 | 82XX S. Kingston Ave. |  |  | 9.5 | 3.6 | 3.8 | 2.3
2017-04-18 | 82XX S. Kingston Ave. |  |  | 7.5 | 7.5 | 28 | 3.0 | 2.8
2017-05-05 | 82XX S. Kingston Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2017-08-01 | 82XX S. Kingston Ave. |  |  | See Follow-Up Sequential Sampling Table for Results
2016-08-24 | 82XX S. Avalon Ave. | Site 2 |  | 1.4 | 7.3 | 5.0 | 1.2
2016-12-15 | 82XX S. Avalon Ave. | Site 2 |  | 1.9 | 3.2 | 3.4 | 1.0
2016-08-25 | 82XX S. Avalon Ave. | Site 3 |  | 7.1 | 14 | 13 | 3.4
2016-12-16 | 82XX S. Avalon Ave. | Site 3 |  | 6.0 | 7.7 | 6.2 | 1.4
2017-01-31 | 82XX S. Avalon Ave. | Site 3 |  | 4.9 | 8.3 | 7.4 | 1.3
2017-02-21 | 82XX S. Avalon Ave. | Site 3 |  | 5.9 | 8.9 | 5.4 | 1.3
2017-03-21 | 82XX S. Avalon Ave. | Site 3 |  | 4.8 | 11 | 10 | 1.4
2017-04-18 | 82XX S. Avalon Ave. | Site 3 |  | 5.1 | 7.1 | 5.9 | 1.5
2017-05-16 | 82XX S. Avalon Ave. | Site 3 |  | 7.9 | 11 | 10 | 2.3
2017-10-10 | 83XX S HOYNE AVE |  |  | 2.2 | 2.0 | 2.1 | 1.0
2017-10-24 | 83XX S HOYNE AVE |  |  | 7.6 | 2.7 | 2.4 | 1.2
2017-05-03 | 8XX N. Lavergne Ave. |  |  | <0.3 | <0.3 | <0.3 | <0.3
2017-09-29 | 8XX N. Lavergne Ave. |  |  | 1.4 | 1.1 | 1.2 | 1.3
2017-11-03 | 8XX N. Lavergne Ave. |  |  | 0.9 | 1.0 | 0.8 | 0.7
2017-11-30 | 8XX N. Lavergne Ave. |  |  | 0.7 | 0.6 | 0.6 | 0.6
2017-12-12 | 8XX N. Lavergne Ave. |  |  | 0.7 | 0.7 | 0.9 | 0.5
2017-07-27 | 89XX S. Hamilton Ave.ˆ |  |  | 4.9 | 4 | 3.8 | 18
2017-09-09 | 89XX S. Hamilton Ave.ˆ |  |  | See Follow-Up Sequential Sampling Table for Results
2017-07-27 | 90XX S. Hamilton Ave. | Site 1 |  | 2.6 | 3.9 | 4.5 | 2.0
2017-07-27 | 90XX S. Hamilton Ave. | Site 2 |  | 3.7 | 5.1 | 4.8 | 3.5
2017-07-27 | 91XX S. Hamilton Ave. |  |  | 3.4 | 4.2 | 3.0 | 2.0
2017-10-05 | 91XX S DREXEL AVE |  |  | 2.0 | 8.6 | 7.6 | 2.2
2017-05-01 | 9XX N. Lavergne Ave. | Site 1 |  | 2.3 | 1.9 | 2.8 | 1.8
2017-09-29 | 9XX N. Lavergne Ave. | Site 1 |  | 4.1 | 2.8 | 6.8 | 3.6
2017-09-15 | 9XX N LEAMINGTON AVE |  |  | 8.6 | 8.4 | 8.7 | 4.6
2017-12-08 | 9XX N LEAMINGTON AVE |  |  | 13 | 11 | 8.1 | 3.1
2017-04-24 | 9XX N. Lavergne Ave. | Site 2 |  | 4.3 | 2.3 | 2.0 | 1.3
2017-09-28 | 9XX N. Lavergne Ave. | Site 2 |  | 3.8 | 3.3 | 3.5 | 2.0
2017-12-22 | 95XX S INDIANA AVE |  |  | 5.2 | 5.5 | 8.8 | 1.1
2017-11-08 | 96XX S CHARLES ST |  |  | 1.5 | 2.5 | 2.5 | 1.3
*Water pressure so low, couldn't take sample at 6th liter
**Samples did not meet study specifications
ˆUnable to obtain full sample set

## Sequential
The results listed on this page are from residential homes in Chicago that have volunteered to have their water tested for lead as part of a research study. The data that is shown below is quality controlled. The study is ongoing, and the results below are a small portion of the large sample population necessary for statistical evaluation. The data below will be further reviewed prior to inclusion in statistical evaluation. The results are anonymized to the block level, so the complete address of each home is not posted. In cases where a sample tests over 15 parts per billion (the action limit set by the EPA), the Department of Water Management will contact the homeowner to discuss the results and schedule a time to resample the water and inspect the home’s plumbing and electrical wiring to better evaluate possible causes. All results are shown in PPB (Parts per Billion). In cases where multiple homes on the same block have results, the location is further amended as "Site 1", "Site 2", etc.
Follow-Up Sequential Sampling |  | Sequential Draws | [9 empty] | Timed Draws
Date Sampled | Address | 1st Draw | 2nd Draw | 3rd Draw | 4th Draw | 5th Draw | 6th Draw | 7th Draw | 8th Draw | 9th Draw | 10th Draw | 3 Minute | 5 Minute | 7 Minute | 10 Minute | 15 Minute
2016-10-08 | 103XX S. Racine Ave. | 2.19 | 2.26 | 4.07 | 3.71 | 9.38 | 15.4 | 11.5 | 10.5 | 11.2 | 10.2 | 8.35 | 4.36
2017-09-06 | 107XX S. Ave. N | 57.1 | 28.7 | 25.1 | 22.1 | 20.2 | 18.9 | 16.8 | 17.6 | 15.4 | 14.1 | 5.32 | 4.28
2017-11-11 | 14XX N. Oakley Blvd. | 8.99 | 5.63 | 6.87 | 23.9 | 18.1 | 12.1 | 17.3 | 11 | 8.41 | 6.96 | 6.39 | 5.23
2017-11-17 | 16XX N. Normandy Ave. | 7.68 | 7.9 | 16.1 | 19.9 | 19.3 | 20.8 | 63.1 | 26 | 26.2 | 27.4 | 21 | 8.7
2018-01-05 | 20XX W. Chase Ave. | 4.46 | 2.99 | 3.48 | 5.18 | 4.56 | 4.52 | 5.94 | 6.8 | 6.71 | 6.69 | 2.65 | 1.74
2017-04-04 | 24XX N. Hamlin Ave.** | 23 | 5.23 | 4.29 | 4.56 | 4.53 | 3.48 | 9.66 | 8.68 | 8.57 | 6.81 | 3.92 | 3.32
2016-11-02 | 25XX N. Keeler Ave. | 5.07 | 5.72 | 3.06 | 2.65 | 6.3 | 11.9 | 25 | 24 | 12.4 | 5.7 | 4.22 | 3.15
2017-08-04 | 26XX N. Drake Ave. Site 2 | 1.61 | 2.1 | 1.65 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
2017-04-07 | 28XX N. Christiana Ave. Site 2 | 10.4 | 15.6 | 14.2 | 11.9 | 11.1 | 10.2 | 9.54 | 8.5 | 8.41 | 6.53 | 5.33 | 4.94 | 4.6 | 4.49 | 4.32
2017-03-03 | 28XX W. 40th St** | 4.07 | 3.18 | 3.16 | 2.4 | 3.44 | 3.92 | 2.6 | 4.04 | 2.73 | 5.05 | 3.05 | 1.36
2017-08-02 | 32XX W Thomas St. | 9.55 | 9.54 | 9.15 | 9.45 | 19.1 | 43.9 | 35.3 | 24.9 | 23.1 | 22.4 | 23.2 | 8.76 | 8.37 | 7.1 | 6.86
2017-09-19 | 32XX N. Nagle Ave. Site 3 | 6.31 | 8.05 | 7.46 | 8.4 | 11.2 | 14.1 | 15.7 | 15.6 | N/A | N/A | 15.2 | 27 | 4.99 | 4.15 | 4.01
2017-07-10 | 34XX S. Marshfield Ave. Site 2 | 24 | 28.8 | 58.2 | 29 | 21.7 | 20.3 | 20.1 | 13.1 | 10.5 | 9.82 | 9.51 | 8.93 | 8.77 | 8.33 | 7.95
2017-06-07 | 36XX S. Paulina St. Site 2 | 6.19 | 2.55 | 4.78 | 2.27 | 2.3 | 2.58 | 4.33 | 2.22 | 2.13 | 2.13 | 1.96 | 1.91
2017-05-27 | 37XX N. Whipple St. Site 1 | 5.2 | 6.06 | 5.11 | 7.11 | 6.05 | 4.51 | 4.96 | 3.55 | 3.49 | 2.22 | 2 | 1.57
2017-05-27 | 38XX N. Whipple St. Site 3 | 13.9 | 23.1 | 39.8 | 26.7 | 27 | 25.3 | 24.9 | 24.7 | 33.1 | 17.4 | 6.18 | 5.3
2017-08-10 | 38XX N. Whipple St. Site 3 | 14.3 | 21.7 | 28.2 | 29.6 | 30.5 | 30 | 33.6 | 38.6 | 34.8 | 32.1 | 10.4 | 8.32 | 8.04 | 7.87 | 7.61
2017-06-07 | 39XX N. Whipple St. Site 1 | 177 | 93.4 | 123 | 110 | 84.1 | 70.9 | 41.5 | 22.7 | 42.5 | 52.9 | 9.93 | 7.82
2017-11-22 | 41XX S. Michigan Ave. | 12.7 | 12.5 | 11.6 | 11.5 | 16.9 | 23.1 | 24.6 | 23.7 | 24.2 | 23.6 | 19.2 | 6.18
2017-11-08 | 42XX N. Hamlin Ave. | 4.45 | 7.35 | 12.3 | 17.1 | 15 | 13.3 | 12.5 | 11.3 | 8.25 | 4.18 | 3.49 | 3.37
2016-10-29 | 45XX N. Albany Ave. Site 2 | 16.3 | 24.3 | 34.7 | 30.5 | 29.9 | 26 | 21.6 | 23.9 | 24.5 | 21.4 | 4.78 | 4.35
2017-09-16 | 45XX N. Whipple St. Site 4 | 6.66 | 15.7 | 31 | 28.2 | 24.3 | 21.2 | 18.8 | 17.1 | 14.9 | 13.1 | 12.6 | 6.06 | 5.59 | 5.59 | 4.76
2017-10-26 | 50XX N WINCHESTER AVE | 8.87 | 9.58 | 9.48 | 7.73 | 8.14 | 9.04 | 8.23 | 7.32 | 6.8 | 7.78 | 6.42 | 6.83 | 6.38 | 5.53 | 5.4
2017-04-29 | 53XX N. Bernard St.** | 3.95 | 10.7 | 17.7 | 15.5 | 14.4 | 13.8 | 12.6 | 9.49 | 5.98 | 3.22 | 3.06 | 1.99
2017-07-15 | 53XX N. Bernard St.** | 7.58 | 8.37 | 8.27 | 8.4 | 8.47 | 8.52 | 8.14 | 7.4 | 7.04 | 6.81 | 6.77 | 5.31
2017-05-17 | 57XX W. Race Ave. | 6.08 | 7.74 | 11.7 | 10.1 | 9.96 | 10.7 | 11 | 9.67 | 12.3 | 6.02 | 5.18 | 4.78
2017-09-29 | 66XX S. Kilpatrick Ave. Site 3 | 1.73 | 23.1 | 4.67 | 4.19 | 4.88 | 3.79 | 2.18 | 2.12 | 1.73 | 1.9 | 2.33 | 1.36
2017-06-09 | 67XX N. Jean Ave. | 2.56 | 3.31 | 4.24 | 10.5 | 13.9 | 14.9 | 17.6 | 12.7 | 19.9 | 21.6 | 4.21 | 2.03
2017-05-05 | 82XX S. Kingston Ave. | 5.54 | 3.96 | 3.06 | 12.5 | 26.9 | 14.2 | 13.2 | 30.9 | 20.6 | 5.13 | 9.49 | 2.79
2017-08-01 | 82XX S. Kingston Ave. | 13.1 | 3 | 3.05 | 3.84 | 6.53 | 8.34 | 11.6 | 9.71 | 9.46 | 14.4 | 8.2 | 3.1 | 3.16 | 2.92 | 2.65
2017-09-09 | 89XX S. Hamilton Ave. | 5.12 | 6.39 | 6.69 | 7.95 | 7.27 | 6.66 | 6.45 | 6.6 | 6.48 | 6.17 | 5.51 | 5
**Samples did not meet study specifications